## Histories
Unverified Histories: Releases Vs Tell-tales AND Verified Reporting: Since 1988
**Note that the unverified histories seldom distinguish between leak tests conducted with fuel and water or controlled releases during leak tests vs UFMs, sample lines, and/or tell-tales. Additional research through verified source documents is/and continues to occur to provide additional/proper context of releases in order to support current/future QRVA/RVAs.
LeakTesting/Repair |  |  | Water |  |  | Water/Fuel |  |  | ND | JP5 | JP8 | DO | Not Specified
Tank 01 | Year ('XX) | 70 | 71 | 71 | 72 | 75 | 82 | 82 | 83 | 83 | 83 |  | Release | Tell-tale
| Period (days) | 63 | 191 | 37 | 56 | 6 | 6 | 55 | 76 | 23 | 38
| Release (gals) | 4623 | 16830 | 5031 | 4810 | 10671 | 2417 | 871 | 2229 | -1090 | -1004 |  | 45388
| Year ('XX) | 47 | 53 | 64 | 65 | 65 | 66 | 67 | 77 | 78 | 78
| Period (days) | 0.0055556 |  | 0.044444 |  |  |  |  | 75 | 114 | 127
| Tell-tale (gals) | 5 | u/k | 0.51 | 0.01 | 0.01 | 0.01 | 0.01 | 999 | 7874 | 13221 |  |  | 22099.55
Tank 02 | Year ('XX)
Period (days)
Release (gals)
| Year ('XX) | 47 | 54 | 54
| Period (days) |  | 0.083333 | 0.29167
| Tell-tale (gals) | u/k | 0.375 | 10
Tank 03 | Year ('XX) | 49
| Period (days) | 71
| Release (gals) | 4260 | [10 empty] | 4260
Year ('XX)
Period (days)
Tell-tale (gals)
Tank 04 | Year ('XX)
Period (days)
Release (gals)
Year ('XX)
Period (days)
Tell-tale (gals)
Tank 05 | Year ('XX) | 14
Period (days)
| Release (gals) | 27000 | [10 empty] | 27000
| Year ('XX) | 64 | 72
| Period (days) | 0.041667 | 1
| Tell-tale (gals) | 1 | 0.5 | [10 empty] | 1.5
Tank 06 | Year ('XX)
Period (days)
Release (gals)
Year ('XX)
Period (days)
Tell-tale (gals)
Tank 07 | Year ('XX) | 81
Period (days)
| Release (gals) | 6505 | [10 empty] | 6505
| Year ('XX) | 78
Period (days)
| Tell-tale (gals) | u/k | [11 empty] | 0
Tank 08 | Year ('XX)
Period (days)
Release (gals)
Year ('XX)
Period (days)
Tell-tale (gals)
Tank 09 | Year ('XX) | 80
| Period (days) | 258
| Release (gals) | 1900 | [10 empty] | 1900
| Year ('XX) | 58
Period (days)
| Tell-tale (gals) | 1500 | [11 empty] | 1500
Tank 10 | Year ('XX) | 80
| Period (days) | 307
| Release (gals) | 3123.1 | [10 empty] | 3123.1 |  | Not mentioned in GPP
| Year ('XX) | 73
| Period (days) | 3
| Tell-tale (gals) | 0.01 | [11 empty] | 0.01
Tank 11 | Year ('XX) | 80
| Period (days) | 34
| Release (gals) | 25628 | [10 empty] | 25628 |  | Higher than GPP of 20,000
Year ('XX)
Period (days)
Tell-tale (gals)
Tank 12 | Year ('XX) | 81
| Period (days) | 2
| Release (gals) | 4280 | [10 empty] | 4280 |  | Undefined in GPP
Year ('XX)
Period (days)
Tell-tale (gals)
Tank 13 | Year ('XX)
Period (days)
Release (gals)
Year ('XX)
Period (days)
Tell-tale (gals)
Tank 14 | Year ('XX)
Period (days)
Release (gals)
Year ('XX)
Period (days)
Tell-tale (gals)
Tank 15 | Year ('XX) | 81
Period (days)
| Release (gals) | u/k | [10 empty] | 0
Year ('XX)
Period (days)
Tell-tale (gals)
Tank 16 | Year ('XX) | 48 | 98 | [11 empty] | 98 release confirmed incorrect
| Period (days) |  | 31 | [11 empty] | per referenced source doc. No
| Release (gals) | u/k | 1469 | [9 empty] | 0 |  | leaks documented in that report.
| Year ('XX) | 49 | 49 | 73 | 81
| Period (days) | 11 | 4
| Tell-tale (gals) | 11009 | 17737 | 0.01 | u/k | [8 empty] | 28746.01
Tank 17 | Year ('XX) | 49
| Period (days) | 71
| Release (gals) | 1420 | [10 empty] | 1420
| Year ('XX) | 69 | 75
| Period (days) | 0.0010417
| Tell-tale (gals) | 1 | u/k | [10 empty] | 1
Tank 18 | Year ('XX)
Period (days)
Release (gals)
Year ('XX)
Period (days)
Tell-tale (gals)
Tank 19 | Year ('XX)
Period (days)
Release (gals)
| Year ('XX) | 64
| Period (days) | 40
| Tell-tale (gals) | 0.66
Tank 20 | Year ('XX)
Period (days)
Release (gals)
Year ('XX)
Period (days)
Tell-tale (gals)
[13 empty] | 119504.1 | 52348.07

## T01_Sources
**Note on the source documents referenced:
Tech Library Unverified Histories: These are original histories that are unstamped/unverified, but were incorrectly cited as references in subsequent reports and became self-verified/referencing.
2014 EPA (Whitacre) Unverified Histories Submission: These were anonymously released/circulated unverified histories that contained the original Tech Library Unverified Histories and additional, more recent unverified histories.
1949 Bechtel Report: Appears to be valid document, but due to age there is no supporting documentation showing acceptance, concurrence, or verification by the US Navy.
2008 Groundwater Protection Plan: This is a summary of the Tech Library Unverified Histories, but not a certification.
1947 | X | Tech Library Unverified Histories | DO from Tell-tale # at rate of 5gal in 8 mins.
| X | 2014 EPA (Whitacre) Unverified Histories Submission | DO from Tell-tale # at rate of 5gal in 8 mins.
1949 Bechtel Report
2008 Groundwater Protection Plan
1953 | X | Tech Library Unverified Histories | DO from Tell-tale 7, rate unkown...drained DO/tested with water...leak found on Tell-tale 7 and crack found in tank.
| X | 2014 EPA (Whitacre) Unverified Histories Submission | DO from Tell-tale 7, rate unkown...drained DO/tested with water...leak found on Tell-tale 7 and crack found in tank.
1949 Bechtel Report
| X | 2008 Groundwater Protection Plan | Leak found on Tell-tale 7 and crack found in tank during cleaning; no leakage rates.
1964 | X | Tech Library Unverified Histories | JP5 from Tell-tale 2 at rate of 1qt in 2.5mins...drawn down then Tell-tale 3 at rate of 1 drop in 10sec and Tell-tale 2...held level for 8 days and Tell-tales 1, 2, 3, 8, 10, 12 showed slow/trace amounts...collector ring was plugged and the cause.
| X | 2014 EPA (Whitacre) Unverified Histories Submission | JP5 from Tell-tale 2 at rate of 1qt in 2.5mins...drawn down then Tell-tale 3 at rate of 1 drop in 10sec and Tell-tale 2...held level for 8 days and Tell-tales 1, 2, 3, 8, 10, 12 showed slow/trace amounts...collector ring was plugged and the cause.
1949 Bechtel Report
| X | 2008 Groundwater Protection Plan | Various leaks from tell-tale; unknown quantity of leakage.
1967 |  | Tech Library Unverified Histories
2014 EPA (Whitacre) Unverified Histories Submission
1949 Bechtel Report
2008 Groundwater Protection Plan