## SummaryAllTanks
OGP - Report No. 434 – 3, March 2010
Atmospheric Storage Tanks Fixed/ floating roof |  |  |  |  | Mean (failures / Year) | 1 Incident / n Yrs
Liquid spill outside tank |  |  |  |  | 0.0028 | 357.1429
Tank rupture |  |  |  |  | 3e-06 | 333333.3333
Generic Distribution from OGP - Report No. 434 – 3, In RISKMAN (Prior)
RM DIST. | Failure Mode | Distribution Type |  |  | Mean (failures / Year) | 1 Incident / n Yrs | 5th | Median | 95th | Range Factor
OGPS | Liquid spill outside tank | Gamma |  |  | 0.00281 | 355.8719 | 9.29e-06 | 0.00116 | 0.00991 | 32.6
OGPL | Tank rupture | Gamma |  |  | 3.01e-06 | 332225.9136 | 9.96e-09 | 1.24e-06 | 1.06e-05 | 32.6
OGPS Updated with Red Hill data
RM DIST. | Failure Mode | Distribution Type |  |  | Mean (failures / Year) | 1 Incident / n Yrs | 5th | Median | 95th | Range Factor
RHOGPS | Small Tank Leaks | One-Stage Update Prior OGPS |  |  | 0.0124 | 80.6452 | 0.00796 | 0.012 | 0.0171 | 1.47
RHOGPL | Large Tank Leaks | One-Stage Update Prior OGPL |  |  | 2.99e-06 | 334448.1605 | 9.99e-09 | 1.23e-06 | 1.05e-05 | 32.6
Bayesian Update Using NavyBulkTank_SpillReleaseData In RISKMAN (7,050 tank years) UST
RM DIST. | Failure Mode | Distribution Type | No. Releases | Tank Years | Mean (failures / Year) | 1 Incident / n Yrs | 5th | Median | 95th | Range Factor
NAVYS | Navy UST Small Releases | One-Stage Update | 10 | 7050 | 0.00145 | 689.6552 | 0.00079 | 0.00138 | 0.00221 | 1.67
NAVYL | Navy UST Large Releases | One-Stage Update | 0 | 7050 | 2.89e-06 | 346020.7612 | 9.6e-09 | 1.19e-06 | 1.02e-05 | 32.6
Second Stage Update Using RedHill Specific Data for Tank 1 - 20 (over 350,640 hours) (Posterior) Using NavyBulkTank_SpillReleaseData (NAVYS prior)
RM DIST. | Failure Mode | Distribution Type | No. Releases | Tank Years | Mean (failures / Year) | 1 Incident / n Yrs | 5th | Median | 95th | Range Factor
RH1S | Tank 1 External Leak Small | Two-Stage Update | 6 | 45.3748 | 0.00238 | 420.1681 | 0.00142 | 0.00221 | 0.00331 | 1.53
RH1L | Tank 1 External Leak Large | Two-Stage Update | 0 |  | 2.89e-06 | 346020.7612 | 9.56e-09 | 1.19e-06 | 1.02e-05 | 32.6
RH2S | Tank 2 External Leak Small | Two-Stage Update | 2 | 68.7428 | 0.00172 | 581.3953 | 0.000969 | 0.00164 | 0.00256 | 1.62
RH2L | Tank 2 External Leak Large | Two-Stage Update | 0 |  | 2.89e-05 | 34602.0761 | 9.56e-09 | 1.19e-09 | 1.02e-05 | 32.6
RH3S | Tank 3 External Leak Small | Two-Stage Update | 1 | 71.7182 | 0.00158 | 632.9114 | 0.000876 | 0.00151 | 0.00238 | 1.65
RH3L | Tank 3 External Leak Large | Two-Stage Update | 0 |  | 2.89e-05 | 34602.0761 | 9.56e-09 | 1.19e-09 | 1.02e-05 | 32.6
RH4S | Tank 4 External Leak Small | Two-Stage Update | 0 | 71.9754 | 0.00144 | 694.4444 | 0.000781 | 0.00137 | 0.00219 | 1.67
RH4L | Tank 4 External Leak Large | Two-Stage Update | 0 |  | 2.89e-05 | 34602.0761 | 9.56e-09 | 1.19e-09 | 1.02e-05 | 32.6
RH5S | Tank 5 External Leak Small | Two-Stage Update | 1 | 64.5937 | 0.00158 | 632.9114 | 0.000877 | 0.00151 | 0.00238 | 1.65
RH5L | Tank 5 External Leak Large | Two-Stage Update | 0 |  | 2.89e-05 | 34602.0761 | 9.56e-09 | 1.19e-09 | 1.02e-05 | 32.6
RH6S | Tank 6 External Leak Small | Two-Stage Update | 1 | 64.1532 | 0.00158 | 632.9114 | 0.000877 | 0.00151 | 0.00238 | 1.65
RH6L | Tank 6 External Leak Large | Two-Stage Update | 0 |  | 2.89e-05 | 34602.0761 | 9.56e-09 | 1.19e-09 | 1.02e-05 | 32.6
RH7S | Tank 7 External Leak Small | Two-Stage Update | 0 | 69.4268 | 0.00144 | 694.4444 | 0.000781 | 0.00137 | 0.00219 | 1.67
RH7L | Tank 7 External Leak Large | Two-Stage Update | 0 |  | 2.89e-05 | 34602.0761 | 9.56e-09 | 1.19e-09 | 1.02e-05 | 32.6
RH8S | Tank 8 External Leak Small | Two-Stage Update | 0 | 70.6252 | 0.00144 | 694.4444 | 0.000781 | 0.00137 | 0.00219 | 1.67
RH8L | Tank 8 External Leak Large | Two-Stage Update | 0 |  | 2.89e-05 | 34602.0761 | 9.56e-09 | 1.19e-09 | 1.02e-05 | 32.6
RH9S | Tank 9 External Leak Small | Two-Stage Update | 1 | 70.9453 | 0.00158 | 632.9114 | 0.000876 | 0.00151 | 0.00238 | 1.65
RH9L | Tank 9 External Leak Large | Two-Stage Update | 0 |  | 2.89e-05 | 34602.0761 | 9.56e-09 | 1.19e-09 | 1.02e-05 | 32.6
RH10S | Tank 10 External Leak Small | Two-Stage Update | 1 | 64.7975 | 0.00158 | 632.9114 | 0.000877 | 0.00151 | 0.00238 | 1.65
RH10L | Tank 10 External Leak Large | Two-Stage Update | 0 |  | 2.89e-05 | 34602.0761 | 9.56e-09 | 1.19e-09 | 1.02e-05 | 32.6
RH11S | Tank 11 External Leak Small | Two-Stage Update | 1 | 71.0999 | 0.00158 | 632.9114 | 0.000876 | 0.00151 | 0.00238 | 1.65
RH11L | Tank 11 External Leak Large | Two-Stage Update | 0 |  | 2.89e-05 | 34602.0761 | 9.56e-09 | 1.19e-09 | 1.02e-05 | 32.6
RH12S | Tank 12 External Leak Small | Two-Stage Update | 0 | 64.4706 | 0.00144 | 694.4444 | 0.000782 | 0.00137 | 0.00219 | 1.67
RH12L | Tank 12 External Leak Large | Two-Stage Update | 0 |  | 2.89e-05 | 34602.0761 | 9.56e-09 | 1.19e-09 | 1.02e-05 | 32.6
RH13S | Tank 13 External Leak Small | Two-Stage Update | 1 | 65.01 | 0.00158 | 632.9114 | 0.000877 | 0.00151 | 0.00238 | 1.65
RH13L | Tank 13 External Leak Large | Two-Stage Update | 0 |  | 2.89e-05 | 34602.0761 | 9.56e-09 | 1.19e-09 | 1.02e-05 | 32.6
RH14S | Tank 14 External Leak Small | Two-Stage Update | 1 | 70.92 | 0.00158 | 632.9114 | 0.000876 | 0.00151 | 0.00238 | 1.65
RH14L | Tank 14 External Leak Large | Two-Stage Update | 0 |  | 2.89e-05 | 34602.0761 | 9.56e-09 | 1.19e-09 | 1.02e-05 | 32.6
RH15S | Tank 15 External Leak Small | Two-Stage Update | 0 | 67.7934 | 0.00144 | 694.4444 | 0.000782 | 0.00137 | 0.00219 | 1.67
RH15L | Tank 15 External Leak Large | Two-Stage Update | 0 |  | 2.89e-05 | 34602.0761 | 9.56e-09 | 1.19e-09 | 1.02e-05 | 32.6
RH16S | Tank 16 External Leak Small | Two-Stage Update | 1 | 68.3953 | 0.00158 | 632.9114 | 0.000876 | 0.00151 | 0.00238 | 1.65
RH16L | Tank 16 External Leak Large | Two-Stage Update | 0 |  | 2.89e-05 | 34602.0761 | 9.56e-09 | 1.19e-09 | 1.02e-05 | 32.6
RH17S | Tank 17 External Leak Small | Two-Stage Update | 1 | 70.33 | 0.00158 | 632.9114 | 0.000876 | 0.00151 | 0.00238 | 1.65
RH17L | Tank 17 External Leak Large | Two-Stage Update | 0 |  | 2.89e-05 | 34602.0761 | 9.56e-09 | 1.19e-09 | 1.02e-05 | 32.6
RH18S | Tank 18 External Leak Small | Two-Stage Update | 0 | 71.015 | 0.00144 | 694.4444 | 0.000781 | 0.00137 | 0.00219 | 1.67
RH18L | Tank 18 External Leak Large | Two-Stage Update | 0 |  | 2.89e-05 | 34602.0761 | 9.56e-09 | 1.19e-09 | 1.02e-05 | 32.6
RH19S | Tank 19 External Leak Small | Two-Stage Update | 0 | 33.264 | 0.00145 | 689.6552 | 0.000786 | 0.00138 | 0.0022 | 1.67
RH19L | Tank 19 External Leak Large | Two-Stage Update | 0 |  | 2.89e-05 | 34602.0761 | 9.56e-09 | 1.19e-09 | 1.02e-05 | 32.6
RH20S | Tank 20 External Leak Small | Two-Stage Update | 0 | 70.9986 | 0.00144 | 694.4444 | 0.000781 | 0.00137 | 0.00219 | 1.67
RH20L | Tank 20 External Leak Large | Two-Stage Update | 0 |  | 2.89e-05 | 34602.0761 | 9.56e-09 | 1.19e-09 | 1.02e-05 | 32.6

## NonInformativeGamma
non-informative prior gamma Red Hill Small < 2 gpm (By Itself)
RM DIST. | Distribution Type | Events | Tank Years | Alpha | Beta |  | λ /yr | 5th | Median | 95th | Range Factor | Source
NONIP | Gamma | 18 | 1315.6499 | 0.5 | 36.5458 |  | 0.0109 | 3.62e-05 | 0.0045 | 0.0386 | 32.6 | Red Hill
Tank 1 - 20 Releases -- Large > 2 gpm
RM DIST. | Distribution Type | Events | Tank Years | Alpha | Beta |  | λ /yr | 5th | Median | 95th | Range Factor | Source
RHLALL | Gamma | 0 | 1315.6499 | 0.5 | 1395.5 |  | 0.000359 | 1.19e-06 | 0.000148 | 1270 | 32.6 | Red Hill
NAVYL | Gamma | 0 | 7050 | 0.5 | 7050 |  | 7.13e-05 | 2.36e-07 | 2.94e-05 | 0.000252 | 32.6 | Navy Bulk Tank Spill Releases Data
NUREG | Gamma |  |  | 0.5 | 1788 |  | 0.000281 | 9.29e-07 | 0.000116 | 0.000991 | 32.6 | NUREC CR 6928
Navy UST -- Small < 2 gpm
| Alpha / Beta = µ |  |  | Alpha | 0.5 |  | µ | 10/7050 | Beta | 0.5*(7050/10)
|  |  |  | Beta | 352
Navy UST -- Small < 2 gpm
RM DIST. | Distribution Type | Events | Tank Years | Alpha | Beta |  | λ /yr | 5th | Median | 95th | Range Factor | Source
NAVYSG | Gamma | 0 |  | 0.5 | 352 |  | 0.00143 | 4.73e-06 | 0.000588 | 0.00504 | 32.6 | Navy Bulk Tank Spill Releases Data
All Red Hill Tanks -- Small < 2 gpm Two-Stage Posterior
RM DIST. | Distribution Type | Events | Tank Years | λ /yr | 5th | Median | 95th | Range Factor | 1 Incident / n Yrs
RHNGPR | One-Stage Update Prior NAVYSG | 18 | 1316 | 0.0111 | 0.00714 | 0.0108 | 0.0154 | 1.47 | 90.0901
RHNVYL | One-Stage Update | 0 | 1316 | 6.01e-05 | 2e-07 | 2.48e-05 | 0.000212 | 32.6 | 16638.9351
All Red Hill Tanks -- Small < 2 gpm plus the Navy UST
RM DIST. | Distribution Type | Events | Tank Years | Alpha | Beta | Beta | λ /yr | 5th | Median | 95th | Range Factor | Source
RHALLS | Gamma | 18 |  | 0.5+18 | 352+1315.6 | 1667.6499 | 0.0111 | 0.00713 | 0.0108 | 0.0153 | 147 | Red Hill "ALL_Tank_RH" tab.
Non-Informative Gamma RedHill Specific Data for Tank 1 - 20 Plus Navy UST
RM DIST. | Failure Mode | Events | Tank Years | Alpha | Beta | Beta | λ /yr | 5th | Median | 95th | Range Factor | 1 Incident / n Yrs
RH1SG | Tank 1 External Leak Small | 6 | 45.3748 | 0.5+6 | 352+45.4 | 397.3748 | 0.0164 | 0.00727 | 0.0152 | 0.0274 | 1.94 | 60.9756
RH2SG | Tank 2 External Leak Small | 2 | 68.7428 | 0.5+2 | 352+68.7 | 420.7428 | 0.00595 | 0.00131 | 0.005 | 0.0126 | 3.11 | 168.0672
RH3SG | Tank 3 External Leak Small | 1 | 71.7182 | 0.5+1 | 352+71.7 | 423.7182 | 0.00354 | 0.000391 | 0.00267 | 0.00875 | 4.73 | 282.4859
RH4SG | Tank 4 External Leak Small | 0 | 71.9754 | 0.5 | 352+72 | 423.9754 | 0.00119 | 3.92e-06 | 0.000488 | 0.00418 | 32.6 | 840.3361
RH5SG | Tank 5 External Leak Small | 1 | 64.5937 | 0.5+1 | 352+64.6 | 416.5937 | 0.0036 | 0.000397 | 0.00271 | 0.0089 | 4.73 | 277.7778
RH6SG | Tank 6 External Leak Small | 1 | 64.1532 | 0.5+1 | 352+64.2 | 416.1532 | 0.00361 | 0.000398 | 0.00272 | 0.00892 | 4.73 | 277.0083
RH7SG | Tank 7 External Leak Small | 0 | 69.4268 | 0.5 | 352+69.4 | 421.4268 | 0.00119 | 3.95e-06 | 0.000492 | 0.00421 | 32.6 | 840.3361
RH8SG | Tank 8 External Leak Small | 0 | 70.6252 | 0.5 | 352+70.6 | 422.6252 | 0.00119 | 3.93e-06 | 0.000489 | 0.00419 | 32.6 | 840.3361
RH9SG | Tank 9 External Leak Small | 1 | 70.9453 | 0.5+1 | 352+70.9 | 422.9453 | 0.00355 | 0.000392 | 0.00267 | 0.00877 | 4.73 | 281.6901
RH10SG | Tank 10 External Leak Small | 1 | 64.7975 | 0.5+1 | 352+64.8 | 416.7975 | 0.0036 | 0.000397 | 0.00271 | 0.0089 | 4.73 | 277.7778
RH11SG | Tank 11 External Leak Small | 1 | 71.0999 | 0.5+1 | 352+71.1 | 423.0999 | 0.00355 | 0.000392 | 0.00267 | 0.00877 | 4.73 | 281.6901
RH12SG | Tank 12 External Leak Small | 0 | 64.4706 | 0.5 | 352+64.5 | 416.4706 | 0.00121 | 4e-06 | 0.000498 | 0.00426 | 32.6 | 826.4463
RH13SG | Tank 13 External Leak Small | 1 | 65.01 | 0.5+1 | 352+66 | 417.01 | 0.0036 | 0.000396 | 0.0027 | 0.00888 | 4.73 | 277.7778
RH14SG | Tank 14 External Leak Small | 1 | 70.92 | 0.5+1 | 352+71.9 | 422.92 | 0.00354 | 0.000391 | 0.00267 | 0.00875 | 4.73 | 282.4859
RH15SG | Tank 15 External Leak Small | 0 | 67.7934 | 0.5 | 352+67.8 | 419.7934 | 0.0012 | 3.96e-06 | 0.000493 | 0.00422 | 32.6 | 833.3333
RH16SG | Tank 16 External Leak Small | 1 | 68.3953 | 0.5+1 | 352+68.4 | 420.3953 | 0.00358 | 0.000394 | 0.00269 | 0.00883 | 4.73 | 279.3296
RH17SG | Tank 17 External Leak Small | 1 | 70.33 | 0.5+1 | 352+71.3 | 422.33 | 0.00355 | 0.000392 | 0.00267 | 0.00877 | 4.73 | 281.6901
RH18SG | Tank 18 External Leak Small | 0 | 71.015 | 0.5 | 352+71 | 423.015 | 0.00119 | 3.93e-06 | 0.000489 | 0.00419 | 32.6 | 840.3361
RH19SG | Tank 19 External Leak Small | 0 | 33.264 | 0.5 | 352+33 | 385.264 | 0.00131 | 4.23e-06 | 0.000538 | 0.00461 | 32.6 | 763.3588
RH20SG | Tank 20 External Leak Small | 0 | 70.9986 | 0.5 | 352+71 | 422.9986 | 0.00119 | 0.000393 | 0.000489 | 0.00419 | 32.6 | 840.3361
0.0027021

## Navy UST Grid
| Low | High
Median | 2e-06 | 0.00117
Range | 2 | 10
Lambda | 1e-05 | 0.1
Emperical
Plant name | Events | Years
Sasebo‐Akasaki | 0 | 100
Sasebo‐Iorizaki | 0 | 128
Sasebo‐Yokose | 1 | 229
Hakozaki | 6 | 998
NB Guam | 1 | 1658
FLC Puget Sound | 0 | 2530
NAS Lemoore | 0 | 748
Guantanamo Bay | 2 | 659
| 10 | 7050
RM DIST. | Distribution Type | λ /yr | 5th | Median | 95th | Range Factor
NGRID | Two Stage Prior | 0.00143 | 3.81e-06 | 2.26e-05 | 0.00458 | 34.6
All Red Hill Tanks -- Small < 1.5 gpm Two-Stage Posterior (prior NGRID)
RM DIST. | Distribution Type | Events | Tank Years | λ /yr | 5th | Median | 95th | Range Factor | 1 Incident / n Yrs
LTKS | Two Stage Posterior | 18 | 1315.6499 | 0.0124 | 0.00678 | 0.0111 | 0.0167 | 1.57 | 80.6452
0.00062
RedHill Specific Data for Tank 1 - 20 Two-Stage Posterior (prior NGRID)
RM DIST. | Failure Mode | Events | Tank Years | λ /yr | 5th | Median | 95th | Range Factor | 1 Incident / n Yrs
RH1S2 | Tank 1 External Leak Small | 6 | 45.3748 | 0.0761 | 0.026 | 0.0713 | 0.107 | 2.01 | 13.1406
RH2S2 | Tank 2 External Leak Small | 2 | 68.7428 | 0.0096 | 0.00012 | 0.00574 | 0.0263 | 14.8 | 104.1667
RH3S2 | Tank 3 External Leak Small | 1 | 71.7182 | 0.00434 | 2.02e-05 | 0.00149 | 0.0121 | 24.5 | 230.4147
RH4S2 | Tank 4 External Leak Small | 0 | 71.9754 | 0.00103 | 3.76e-06 | 1.94e-05 | 0.00308 | 28.6 | 970.8738
RH5S2 | Tank 5 External Leak Small | 1 | 64.5937 | 0.00451 | 2.14e-05 | 0.00163 | 0.0127 | 24.2 | 221.7295
RH6S2 | Tank 6 External Leak Small | 1 | 64.1532 | 0.00452 | 2.15e-05 | 0.00164 | 0.0128 | 24.4 | 221.2389
RH7S2 | Tank 7 External Leak Small | 0 | 69.4268 | 0.00104 | 3.76e-06 | 1.95e-05 | 0.00312 | 28.8 | 961.5385
RH8S2 | Tank 8 External Leak Small | 0 | 70.6252 | 0.00103 | 3.76e-06 | 1.95e-05 | 0.0031 | 28.7 | 970.8738
RH9S2 | Tank 9 External Leak Small | 1 | 70.9453 | 0.00436 | 2.03e-05 | 0.0015 | 0.0121 | 24.5 | 229.3578
RH10S2 | Tank 10 External Leak Small | 1 | 64.7975 | 0.0045 | 2.13e-05 | 0.00162 | 0.0127 | 24.4 | 222.2222
RH11S2 | Tank 11 External Leak Small | 1 | 71.0999 | 0.00436 | 2.03e-05 | 0.0015 | 0.0121 | 24.5 | 229.3578
RH12S2 | Tank 12 External Leak Small | 0 | 64.4706 | 0.00105 | 3.76e-06 | 1.97e-05 | 0.00319 | 29.1 | 952.381
RH13S2 | Tank 13 External Leak Small | 1 | 65.01 | 0.00447 | 2.11e-05 | 0.0016 | 0.0126 | 24.4 | 223.7136
RH14S2 | Tank 14 External Leak Small | 1 | 70.92 | 0.00434 | 2.01e-05 | 0.00149 | 0.0121 | 24.5 | 230.4147
RH15S2 | Tank 15 External Leak Small | 0 | 67.7934 | 0.00104 | 3.76e-06 | 1.96e-05 | 0.00314 | 28.9 | 961.5385
RH16S2 | Tank 16 External Leak Small | 1 | 68.3953 | 0.00442 | 2.07e-05 | 0.00155 | 0.0124 | 24.4 | 226.2443
RH17S2 | Tank 17 External Leak Small | 1 | 70.33 | 0.00435 | 2.02e-05 | 0.0015 | 0.0121 | 24.5 | 229.8851
RH18S2 | Tank 18 External Leak Small | 0 | 71.015 | 0.00103 | 3.76e-06 | 1.95e-05 | 0.00309 | 28.7 | 970.8738
RH19S2 | Tank 19 External Leak Small | 0 | 33.264 | 0.00119 | 3.78e-06 | 2.09e-05 | 0.00371 | 31.3 | 840.3361
RH20S2 | Tank 20 External Leak Small | 0 | 70.9986 | 0.00103 | 3.76e-06 | 1.95e-05 | 0.00309 | 28.7 | 970.8738
0.0069155

## Navy UST Grid Large
| Low | High
Median | 2e-05 | 4e-05
Range | 15 | 40
Lambda | 2e-06 | 0.0001
Emperical
Plant name | Events | Years
Sasebo‐Akasaki | 0 | 100
Sasebo‐Iorizaki | 0 | 128
Sasebo‐Yokose | 0 | 229
Hakozaki | 0 | 998
NB Guam | 0 | 1658
FLC Puget Sound | 0 | 2530
NAS Lemoore | 0 | 748
Guantanamo Bay | 0 | 659
7050
RM DIST. | Distribution Type | λ /yr | 5th | Median | 95th | Range Factor
NAVYLG | Two Stage Prior | 7.63 | 8L7E-7 | 2.77e-05 | 0.000136 | 12.5
All Red Hill Tanks -- Small > 1.5 gpm Two-Stage Posterior (prior NAVYLG)
RM DIST. | Distribution Type | Events | Tank Years | λ /yr | 5th | Median | 95th | Range Factor | 1 Incident / n Yrs
RHLNG | Two Stage Posterior | 0 | 1315.6499 | 6.65e-05 | 8.7e-07 | 2.26e-05 | 0.000134 | 12.4 | 15037.594

## RedHill Release Incidents
| Date | Tank | Verified / Unverified | Verified - Period (days) | Verfied - Release (gals) | Verified - Rate (gpm) | Verified - Tell-Tale (gals) | Verified - Tell-Tale Rate (gpm) | Verfied - Type | Verified - During Leak Test | Height | Liquid Level | TELLTALE | !TT and !Test | TIR | Evolution Type | Small < 2(gph) / Large > 2(gph) | Unverified - Quantity (gallons) | Unverified - Rate | Small < 2(gph) / Large > 2(gph) | Type | Detection Method | Mitigation | Cause | Data Source | Extracts from EPA-R09-UST-2015-0441-0559 (1).pdf:
1947 | 1947 | 1 | V | 0.006 |  |  | 5 | 0.5787 | DO | No |  |  | TT | 0 | OP | OP | Small |  | 0.625 gallons / minute | Small | JP-5 | Telltale |  |  | EPA-R09-UST-2015-0441-0559 (1).pdf RH_Tank01_UnverifiedHistory.PDF RH_Tank02_UnverifiedHistory.PDF RH_CompUnverLeakHistories_DEC17.xlsx Whitacre 2014b.pdf | Misreport of Tank 1 and 2 in EPA-R09-UST-2015-0441-0559 (1).pdf: "Tanks #1 and #2 leaks reported (Whitacre, 2014b). Diesel oil draining from Tank #1 telltale at a rate of 0.625 gallons per minute (Whitacre, 2014b)." Witacre 2014b.pdf: "The attached documents construction, repairs and historical releases for Red Hill Tank #1."
1947 | 1947 Oct. | 2 | V |  |  |  | u/k |  | DO | No |  |  | TT | 0 | OP | OP | Small |  |  | Small | JP-5 | telltale | tank emptied |  | RH_Tank02_UnverifiedHistory.PDF EPA-R09-UST-2015-0441-0559 (1).pdf RH_CompUnverLeakHistories_DEC17.xlsx Whitacre 2014h.pdf | Correct report for Tank 2: "Tank #2 telltale leak of unknown severity noted; tank emptied (TEC, 2008; Whitacre, 2014h)."
1948 | 1948 Jul. 1949 | 16 | V | 11 |  |  | 11009 | 0.69501 | DO | Yes |  |  | TT | 0 | OP | OP | Small | 11000 |  | Small |  | telltale | tank emptied |  | RH_Tank16_UnverifiedHistory.PDF EPA-R09-UST-2015-0441-0559 (1).pdf Tank 16 API653 Final Inspection Report_2007.pdf 2007 RH_CompUnverLeakHistories_DEC17.xlsx | "Tank #16 telltale leak noted; tank emptied (TEC, 2008)." "Tank #16 telltale leak. Level down 2.25-inches in 11 days (approximately 11,000 gallons lost) (TEC, 2008)."
1949 | 1949 | 17 | V | 71 | 1420 | 0.013889 |  |  |  | Yes | NOT PROVIDED | NOT PROVIDED | !TT | 0 | OP | OP | Small | [7 empty] | RH_CompUnverLeakHistories_DEC17.xlsx Whitacre 2014g.pdf
1949 | 1949 | 3 | V | 71 | 4260 | 0.041667 |  |  | DO | No | NOT PROVIDED | NOT PROVIDED | !TT | 1 | OP | OP | Small | [7 empty] | RH_CompUnverLeakHistories_DEC17.xlsx Whitacre 2014h.pdf
1949 | 1949 Dec. | 16 | V | 4 |  |  | 17737 | 3.0793 | DO | Yes |  |  | TT | 0 | OP | OP | Small | 18000 |  | Small |  | telltale |  |  | RH_Tank16_UnverifiedHistory.PDF EPA-R09-UST-2015-0441-0559 (1).pdf RH_CompUnverLeakHistories_DEC17.xlsx | "Tank #16 was refilled and the level decreased 3.63-inches in about four days, indicating a loss of about 18,000 gallons. No information was given as to when the leakage was stopped (TEC, 2008)."
1952 | 1952-07-23 | 6 | U | [9 empty] | TT | 0 | OP | OP | Small |  |  | operating |  | Telltale |  |  | BWS comments on AOC Redhill_API653Report_Tank06_Jan07.pdf Final API 653 Inspection Report-Tk 6_2007.pdf
1953 | 1953 Aug. | 1 | V |  |  |  | U/k |  | Water | Yes |  |  | TT | 0 |  | OP | Small |  |  | Small | JP-5 | crack found in tank |  | crack found in tank | RH_Tank01_UnverifiedHistory.PDF EPA-R09-UST-2015-0441-0559 (1).pdf RH_CompUnverLeakHistories_DEC17.xlsx Whitacre 2014b.pdf | "Tank #1 leak found on telltale number 7; crack found in tank (TEC, 2008; Whitacre, 2014b)."
1954 | 1954 May | 2 | V | 0.083 |  |  | 0.375 | 0.0031376 | DO | No |  |  | TT | 0 | OP | Unknown | Small |  | 10 gallons in 7 hours | Small | JP-5 |  |  |  | EPA-R09-UST-2015-0441-0559 (1).pdf RH_Tank02_UnverifiedHistory.PDF RH_CompUnverLeakHistories_DEC17.xlsx Whitacre 2014h.pdf | "Tank #2 second leak found. Reported leak rates of 3 pints in 2 hours and 10 gallons in 7 hours; no reported estimate of volume loss (Whitacre, 2014h)."
1954 | 1954 | 2 | V | 0.292 |  |  | 10 | 0.023782 | Water | No |  |  | TT | 0 |  | OP | Small | [7 empty] | RH_CompUnverLeakHistories_DEC17.xlsx Whitacre 2014h.pdf
1958 | 1958 Apr. | 9 | V |  |  |  | 1500 |  |  | No |  |  | TT | 0 | OP | OP | Small | 1500 |  | Small | DFM | telltale |  |  | RH_Tank09_UnverifiedHistory.PDF EPA-R09-UST-2015-0441-0559 (1).pdf RH_CompUnverLeakHistories_DEC17.xlsx | "Tank #9 leaked approximately 1,500 gallons from telltale in the Apr. to May timeframe (TEC, 2008)."
| 1964 Jan. | 12 (Dome Section) | U (Dome Section) | [6 empty] | (No) |  |  | (!TT) | [7 empty] | DFM |  |  | dome section leak identified | RH_Tank12_UnverifiedHistory.PDF EPA-R09-UST-2015-0441-0559 (1).pdf Whitacre, 2014e | "Tank #12 dome section leak identified; no evidence of corrosion on bottom plates or piping (TEC, 2008; Whitacre, 2014e). Tank #11 found to be in good condition, with no evidence of liner plate corrosion in bottom section (Whitacre, 2014e)."
1964 | 1964 Jun. | 19 | V | 40 |  |  | 0.66 | 1.1458e-05 | JP5 | No |  |  | TT | 0 | OP | OP | Small |  | 5 mL/hr. | Small | JP-5 | telltale |  | weld leak discovered, | RH_Tank19_UnverifiedHistory.PDF EPA-R09-UST-2015-0441-0559 (1).pdf RH_CompUnverLeakHistories_DEC17.xlsx Whitacre 2014i.pdf | "Tank #19 weld leak discovered (Whitacre, 2014i). The telltale leak was estimated to be about 5 mL/hr. Other small holes discovered during inspection were repaired (TEC, 2008; Whitacre, 2014i)."
1964 | 1964 Aug. | 1 | V | 0.003 |  |  | 0.25 | 0.05787 | ND | No |  |  | TT | 0 | OP | OP | Small |  | 1 quart per 2.5 minutes | Small | JP-5 |  |  |  | RH_Tank01_UnverifiedHistory.PDF EPA-R09-UST-2015-0441-0559 (1).pdf RH_CompUnverLeakHistories_DEC17.xlsx Whitacre 2014b.pdf | "Tank #1 leak discovered (1 quart per 2.5 minutes) (Whitacre, 2014b)."
1964 | 1964 | 1 | V | 0.042 |  |  | 0.25 | 0.0041336 | ND | No |  |  | TT | 0 | OP | OP | Small | [7 empty] | RH_CompUnverLeakHistories_DEC17.xlsx
1964 | 1964 | 1 | V |  |  |  | 0.01 |  | ND | No |  |  | TT | 0 | OP | OP | Small | [7 empty] | RH_CompUnverLeakHistories_DEC17.xlsx
1964 | 1964 | 5 | V | 0.042 |  |  | 1 | 0.016534 | JP5 | No |  |  | TT | 0 | OP | OP | Small | [7 empty] | RH_CompUnverLeakHistories_DEC17.xlsx Whitacre 2014h.pdf
1965 | 1965 | 1 | V |  |  |  | 0.01 |  | JP5 | Yes |  |  | TT | 0 | OP | OP | Small | [7 empty] | RH_CompUnverLeakHistories_DEC17.xlsx
1965 | 1965 | 1 | V |  |  |  | 0.01 |  | Water | No |  |  | TT | 0 |  | OP | Small | [7 empty] | RH_CompUnverLeakHistories_DEC17.xlsx
1966 | 1966 | 1 | V |  |  |  | 0.01 |  | Water/Fuel | No |  |  | TT | 0 |  | OP | Small | [7 empty] | RH_Tank05_UnverifiedHistory.PDF EPA-R09-UST-2015-0441-0559 (1).pdf RH_CompUnverLeakHistories_DEC17.xlsx Whitacre 2014b.pdf
1967 | 1967 | 1 | V |  |  |  | 0.01 |  | Water | No |  |  | TT | 0 |  | OP | Small | [7 empty] | RH_CompUnverLeakHistories_DEC17.xlsx
1965 | 1965 Mar. | 5 | V |  |  |  | 1 | 0.013333 |  | No |  |  | TT | 0 | OP | OP | Small |  | 1 gallon per 1.25 hours | Small | JP-5 |  |  |  | RH_Tank05_UnverifiedHistory.PDF Whitacre 2014h.pdf | "Tank #5 exhibits suspected leak in telltale system (1 gallon per 1.25 hours); tank was worked on intermittently for six months, but no leak found. It was suspected that the leak “partially rusted over” (Whitacre, 2014h)."
1969 | 1969 Jun. | 17 | V | 0.001 |  |  | 1 | 0.69444 | JP5 | No |  |  | TT | 0 | OP | OP | Small |  | gallon per 1.5 minutes | Small | JP-5 | telltale |  |  | RH_Tank17_UnverifiedHistory.PDF EPA-R09-UST-2015-0441-0559 (1).pdf RH_CompUnverLeakHistories_DEC17.xlsx Whitacre 2014g.pdf | "Tank #17 reported as leaking about 1 gallon per 1.5 minutes based on telltale. Fuel was transferred (TEC, 2008; Whitacre, 2014g)."
1970 | 1970 Aug. | 1 | V | 63 | 4623 | 0.050959 |  |  | JP5 | No | NOT PROVIDED | 230'-5-1/4" to 230'-2" | !TT | 1 | OP | OP | Small | 31294 | over(Aug. 1970 and Apr. 1972) | Small | JP-5 | unexplained fuel drops |  |  | RH_Tank01_UnverifiedHistory.PDF EPA-R09-UST-2015-0441-0559 (1).pdf RH_CompUnverLeakHistories_DEC17.xlsx Whitacre 2014b.pdf | "Tank #1 exhibited unexplained fuel drops amounting to 31,294 gallons between Aug. 1970 and Apr. 1972 (TEC, 2008; Whitacre, 2014b)."
1971 | 1971 | 1 | V | 191 | 16830 | 0.061191 |  |  | JP5 | No | NOT PROVIDED | 230'-1" to 229'-1-7/8" | !TT | 1 | OP | OP | Small | [7 empty] | RH_CompUnverLeakHistories_DEC17.xlsx
1971 | 1971 | 1 | V | 37 | 5031 | 0.094426 |  |  | JP5 | No | NOT PROVIDED | 230'-8-1/4" to 230'-4-5/8" | !TT | 1 | OP | OP | Small | [7 empty] | RH_CompUnverLeakHistories_DEC17.xlsx
1972 | 1972 | 1 | V | 56 | 4810 | 0.059648 |  |  | JP5 | No | NOT PROVIDED | 230'-9-1/4" to 230'-0-1/4" | !TT | 1 | OP | OP | Small | [7 empty] | RH_CompUnverLeakHistories_DEC17.xlsx
1972 | 1972 Feb. | 5 | V | 1 |  |  | 0.5 | 0.00034722 | JP5 | No |  |  | TT | 0 | OP | OP | Small |  | 2 quarts per day | Small | JP-5 | telltale |  |  | RH_Tank05_UnverifiedHistory.PDF EPA-R09-UST-2015-0441-0559 (1).pdf RH_CompUnverLeakHistories_DEC17.xlsx Whitacre 2014h.pdf | "Tank #5 telltale leak at 2 quarts per day; response uncertain (TEC, 2008; Whitacre, 2014h)."
1973 | 1973 Jan. | 10 | V | 3 |  |  | 0.01 |  |  | No | NOT PROVIDED | NOT PROVIDED | !TT | 1 | OP | OP | Small |  |  | Small | DFM | leak suspected | tank emptied |  | RH_Tank10_UnverifiedHistory.PDF EPA-R09-UST-2015-0441-0559 (1).pdf RedHill_Tank10InspectionReport_1998.pdf RH_CompUnverLeakHistories_DEC17.xlsx Whitacre 2014d.pdf | "Tank #10 leak suspected; tank emptied (TEC, 2008; Whitacre, 2014d)."
1973 | 1973 May | 16 | V | 0.01 |  |  |  |  | JP5 | No |  |  | TT | 0 | OP | OP | Small |  | 1 drop per 20 seconds | Small |  | telltale |  |  | RH_Tank16_UnverifiedHistory.PDF EPA-R09-UST-2015-0441-0559 (1).pdf RedHill_API653Report_tank16_jan07.pdf RH_CompUnverLeakHistories_DEC17.xlsx | "Tank #16 telltale leak of 1 drop per 20 seconds (TEC, 2008)."
1973 | 1973 Mar. | 12 | U (Suspected but not comfirmed) | [6 empty] | No |  |  | !TT | 1 |  |  | Small |  |  | Small | DFM | suspected leak | tank emptied |  | RH_Tank12_UnverifiedHistory.PDF EPA-R09-UST-2015-0441-0559 (1).pdf Whitacre 2014e.pdf | "Tank #12 emptied due to suspected leak (TEC, 2008)."
1973 | 1973 Nov. | 7 | U | [6 empty] | No |  |  | TT | 0 | OP | OP | Small |  |  | Small | DFM | telltale | tank emptied |  | RH_Tank07_UnverifiedHistory.PDF EPA-R09-UST-2015-0441-0559 (1).pdf RedHill_Tank07Inspection Report_1998.pdf | "Tank #7 telltale leak (possibly only internal); tank emptied (TEC, 2008)."
1975 | 1975 Jan. | 17 | V |  |  |  | U/k |  |  | No |  |  | TT | 0 | OP | OP | Small |  |  | Small | JP-5 | telltale |  |  | RH_Tank17_UnverifiedHistory.PDF EPA-R09-UST-2015-0441-0559 (1).pdf RH_CompUnverLeakHistories_DEC17.xlsx Whitacre 2014g.pdf | "Tank #16 was emptied (TEC, 2008). Tank #17 started leaking based on telltale (Whitacre, 2014g)."
1975 | 1975 May | 1 | V | 6 | 10671 | 1.2351 |  |  | JP5 | No | At 184.750' tank level stops dropping | 189.989' to 189.807' | !TT | 1 | OP | OP | Small | 32765 | over(May 1975 and Aug. 1978) | Small | JP-5 | unexplained fuel drops |  |  | RH_Tank01_UnverifiedHistory.PDF EPA-R09-UST-2015-0441-0559 (1).pdf RH_CompUnverLeakHistories_DEC17.xlsx Whitacre 2014b.pdf | "Tank #1 exhibited unexplained fuel drops amounting to 32,765 gallons between May 1975 and Aug. 1978 (TEC, 2008; Whitacre, 2014b)."
1976 | 1976 Apr. | 10 | U | [6 empty] | No |  |  | TT | 0 | OP | OP | Small |  |  | Small | DFM | telltale | tank emptied |  | RH_Tank10_UnverifiedHistory.PDF EPA-R09-UST-2015-0441-0559 (1).pdf RedHill_Tank10InspectionReport_1998.pdf Whitacre 2014d.pdf | "Tank #10 was emptied and removed from service as a result of a leak detected from telltale (TEC, 2008; Whitacre, 2014d)."
1976 | 1976 May | 13 | U | [6 empty] | No | NOT PROVIDED | NOT PROVIDED | !TT | 1 | OP | OP | Small |  |  | Small | DFM | reported as leaking |  |  | RH_Tank13_UnverifiedHistory.PDF EPA-R09-UST-2015-0441-0559 (1).pdf Whitacre 2014e.pdf | "Tank #13 reported as leaking (TEC, 2008; Whitacre, 2014e)."
1977 | 1977 | 1 | V | 75 |  |  | 999 | 0.00925 | JP5 | No |  |  | TT | 0 | OP | OP | Small | [7 empty] | RH_CompUnverLeakHistories_DEC17.xlsx
1978 | 1978 | 1 | V | 114 |  |  | 7874 | 0.047965 | JP5 | No |  |  | TT | 0 | OP | OP | Small | [7 empty] | RH_CompUnverLeakHistories_DEC17.xlsx
1978 | 1978 | 1 | V | 127 |  |  | 13221 | 0.072293 | JP5 | No |  |  | TT | 0 | OP | OP | Small | [7 empty] | RH_CompUnverLeakHistories_DEC17.xlsx
1978 | 1978 May | 7 | V |  |  |  | U/K |  | JP5 | No |  |  | TT | 0 | OP | OP | Small |  | significant telltale leak | Small | DFM | telltale | tank emptied |  | RH_Tank07_UnverifiedHistory.PDF EPA-R09-UST-2015-0441-0559 (1).pdf RedHill_Tank07Inspection Report_1998.pdf RH_CompUnverLeakHistories_DEC17.xlsx | "Tank #7 exhibits significant telltale leak; tank emptied (TEC, 2008; Whitacre, 2014c)."
1978 | 1978 Jul. | 9 | U | [6 empty] | No | NOT PROVIDED | NOT PROVIDED | !TT | 1 | TIR | RTS | Small |  | 4.5 to 17.9 gallons/day | Small | DFM | Leak test | no documentation of any actions taken to mitigate | after the repair project | RH_Tank09_UnverifiedHistory.PDF EPA-R09-UST-2015-0441-0559 (1).pdf | "Tank #9 repair performed from Jul. 1978 to Feb. 1981; telemetering system installed. Leak test rates after the repair project were reported to range from 4.5 to 17.9 gallons/day; no documentation of any actions taken to mitigate Tank #9 leak(s) (TEC, 2008)."
1980 | 1980 | 9 | V | 258 | 1900 | 0.0051141 |  |  |  | Yes | NOT PROVIDED | NOT PROVIDED | !TT | 0 | OP | OP | Small | [7 empty] | RH_CompUnverLeakHistories_DEC17.xlsx
1980 | 1980 | 10 | V | 307 | 3123 | 0.0070643 |  |  |  | Yes | NOT PROVIDED | NOT PROVIDED | !TT | 0 | TIR | OP | Small | [7 empty] | RH_CompUnverLeakHistories_DEC17.xlsx Whitacre 2014d.pdf
1980 | 1980 Aug. | 11 | V | 34 | 25628 | 0.52345 |  |  | JP5 | Yes | the current level of 51 feet and bottom of the tank | filled to capacity | !TT | 0 | OP | OP | Small | 15000 | 10,000 to 20,000 gallons 1,000 to 1,500 gallons per day other source has peak leak rate at 2412 gal/day while at 214' | Small | DFM |  | emptied and repaired |  | RH_Tank11_UnverifiedHistory.PDF EPA-R09-UST-2015-0441-0559 (1).pdf RH_CompUnverLeakHistories_DEC17.xlsx Whitacre 2014e.pdf | "Tank #11 reported to be leaking 1,000 to 1,500 gallons per day according to Whitacre (2014e) and 165 to 2,412 gallons per day (Anonymous, Undated). Leak location determined to be at 51 feet from bottom of tank . Repairs made. Based on these volumetric flow rates, fuel loss was estimated to be between 10,000 to 20,000 gallons (TEC, 2008)."
1981 | 1981 | 7 | V |  | 6505 |  |  |  |  | Yes | NOT PROVIDED | dropped to 207.0 feet | !TT | 0 | TIR | RTS | Small | 6505 | leak occurred during refilling which began on 2/20/1980 at 235' 609gal/day, rate dropped to< 13 gallons per day below 207 foot fill level | Small | DFM |  |  | Look at Tank 7 Inspection report. | RH_Tank07_UnverifiedHistory.PDF EPA-R09-UST-2015-0441-0559 (1).pdf RedHill_Tank07Inspection Report_1998.pdf RH_CompUnverLeakHistories_DEC17.xlsx | "Tank #7 leak rate after filling measured, and approximately “6,505 gallons leakage measured until rate dropped to< 13 gallons per day below 207 foot fill level” (TEC, 2008; Whitacre, 2014c)."
1981 | 1981 | 16 | V |  |  |  | U/K |  | JP5 | Yes |  |  | TT | 0 | TIR | RTS | Small |  | leaking badly | Small |  |  |  | after repairs when filled to 242-foot level. | RH_Tank16_UnverifiedHistory.PDF EPA-R09-UST-2015-0441-0559 (1).pdf RH_CompUnverLeakHistories_DEC17.xlsx | "Tank #16 was found to be leaking badly after repairs when filled to 242-foot level (Anonymous, Undated)."
1981 | 1981 Jan. | 10 | U | [6 empty] | No | Leak located between 239 ft. and 240 ft. level. | 235.0 ft. to 242.1 ft. This leak could be the same as in 1980 | !TT | 1 | TIR | RTS | Small |  | severe leak near the top of the tank (between the 235- and 242-foot level) | Small | DFM |  | tank emptied | Look at Tank 10 Inspection report From 1998 | RH_Tank10_UnverifiedHistory.PDF EPA-R09-UST-2015-0441-0559 (1).pdf RedHill_Tank10InspectionReport_1998.pdf Whitacre 2014d.pdf | "Tank #10 found to have a severe leak near the top of the tank (between the 235- and 242-foot level) during refill (TEC, 2008). Fuel ran out on the concrete near the first platform on the stairway to top of dome; tank emptied (TEC, 2008; Whitacre, 2014d)."
1981 | 1981 Feb. | 12 | V | 2 | 4280 | 1.4861 |  |  |  | Yes | NOT PROVIDED | Tank was refilled to 100" level and leaked at a rate of 1400 gallons per day. | !TT | 0 | TIR | RTS | Small |  | 1,440 gallons per day at the 100-foot level | Small | DFM |  |  | after repairs | RH_Tank12_UnverifiedHistory.PDF EPA-R09-UST-2015-0441-0559 (1).pdf RH_CompUnverLeakHistories_DEC17.xlsx Whitacre 2014e.pdf | "Tank #12 was found to be leaking at a rate of 1,440 gallons per day after repairs at the 100-foot level (TEC, 2008; Whitacre, 2014e). Tank #12 returned to service after leak testing (Whitacre, 2014e)."
1981 | 1981 Jul. | 15 | V |  | U/K |  |  |  |  | Yes |  | filled to 185' level and showed leakage | !TT | 0 | TIR | RTS | Small |  | leaking badly | Small | DFM |  |  | after tank repair and lining | RH_Tank15_UnverifiedHistory.PDF EPA-R09-UST-2015-0441-0559 (1).pdf RH_CompUnverLeakHistories_DEC17.xlsx API-653 Inspection Report-Tk15_2007.pdf Whitacre 2014f.pdf | "Tank #15 found to be leaking badly upon refilling after tank repair and lining (TEC, 2008; Whitacre, 2014f)." (1981 Jul) "Tank #15 removed from service from Aug. to Oct. 1981. Following repair, leak testing showed continued leaking; tank repaired again (TEC, 2008)." (1981 Aug. )
1981 | 1981 Sep | 13 | U (Don) |  | U/K | [6 empty] | Tank was filled and leaks above 188 foo level. | !TT |  | TIR | RTS | Small |  |  | RTS |  |  |  | RTS | EPA-R09-UST-2015-0441-0559(1).pdf, BWS comments on AOC Whitacre 2014e.pdf | "Tank #13 returned to service after lining and repairs; leaks found above the 188-foot level and repaired (TEC, 2008; Whitacre, 2014e)."
1981 | 1981 Oct. | 16 | V |  | u/k |  |  |  |  | No |  |  | TT | 0 | TIR | RTS | Small |  | leaking badly | Small |  |  |  | after repairs and lining | RH_Tank16_UnverifiedHistory.PDF EPA-R09-UST-2015-0441-0559 (1).pdf
1982 | 1982 Feb | 14 | U | [7 empty] | NOT PROVIDED | NOT PROVIDED | !TT |  | OP | OP | Small |  | maybe? | operating |  |  |  | Tank was removed from service for leak repairs. | EPA-R09-UST-2015-0441-0559(1).pdf, BWS comments on AOC Whitacre 2014f.pdf | "Tank #14 removed from service for leak repairs (Whitacre, 2014f)."
1982 | 1982 July | 1 | V | 6 | 2417 | 0.27975 |  |  | JP5 | Yes | NOT PROVIDED | 229.990' to 229.853' 200.990' to 200.974' | !TT | 0 | OP | OP | Small | 5517 | over (Jul. 1982 to Jan. 1983) | Small | JP-5 | drops in fuel level |  |  | RH_Tank01_UnverifiedHistory.PDF EPA-R09-UST-2015-0441-0559 (1).pdf RH_CompUnverLeakHistories_DEC17.xlsx Whitacre 2014b.pdf | "Tank #1 estimated as having leaked 5,517 gallons from Jul. 1982 to Jan. 1983 based on drops in fuel level (TEC, 2008; Whitacre, 2014b)."
1982 | 1982 | 1 | V | 55 | 871 | 0.010997 |  |  | JP5 | Yes | NOT PROVIDED | 229.852' to 229.728' | !TT | 0 | TIR | RTS | Small | [7 empty] | RH_CompUnverLeakHistories_DEC17.xlsx
1983 | 1983 | 1 | V | 77 | 2229 | 0.020103 |  |  | JP5 | Yes | NOT PROVIDED | 230.107' to 230.170 for a gain of 1090.2 gal | !TT | 0 | TIR | RTS | Small | [7 empty] | RH_CompUnverLeakHistories_DEC17.xlsx
| 1983 | 1 (Back Seapage) | V (Back Seapage) | 23 | -1090 | -0.032911 |  |  | JP5 | (Yes) |  |  |  | 0 |  | RTS | [8 empty] | RH_CompUnverLeakHistories_DEC17.xlsx
| 1983 | 1 (Back Seepage) | V (Back Seapage) | 38 | -1004 | -0.018348 |  |  | JP5 | (Yes) |  |  |  | 0 |  | RTS | [8 empty] | RH_CompUnverLeakHistories_DEC17.xlsx
| 1998 | 19 (During Maint.) | U (During Maint.) | [6 empty] | No | [5 empty] | RTS |  |  |  |  | JP-5 | back seepage |  | Observed in Tank Mainteance project | EPA-R09-UST-2015-0441-0559 (1).pdf Whitacre 2014i.pdf | "Tank #19 “back seepage” observed during tank maintenance project (TEC, 2008)."
1998 | 1998 Oct. | 16 | V | 31 | 1469 | 0.032908 |  |  |  | No | NOT PROVIDED | 109.099' to 109.074' | !TT | 1 | OP | OP | Small | 1469 | 71 gal/day (over 30.7 days) | Small |  | Tank level drop; petroleum found under base of tank | tank emptied |  | EPA-R09-UST-2015-0441-0559 (1).pdf RedHill_API653Report_tank16_jan07.pdf RH_CompUnverLeakHistories_DEC17.xlsx Whitacre 2014a.pdf | "Tank #16 experienced a loss of 1,469 gallons (71 gal/day) over 30.7 days (Whitacre, 2014a). Cores removed from under the center of Tank #16 found to smell of fuel and contain oily sludge-like material (Whitacre, 2014a). Tank #16 emptied from Oct. to Nov. due to concerns over tank level drop; petroleum found under base of tank (Whitacre, 2014a)."
1999 | 1999 Sep. | 1 | U | [6 empty] | No |  |  | TT | 0 | OP | OP | Small |  | steady stream | Small | JP-5 | Leak into Lower Access Tunnel |  | Tank #1 telltale pipe number 11 found to be leaking a steady stream into the Lower Access Tunnel. The pipe was capped to stop the leak (Whitacre, 2014b). | EPA-R09-UST-2015-0441-0559 (1).pdf Whitacre 2014b.pdf | "Tank #1 telltale pipe number 11 found to be leaking a steady stream into the Lower Access Tunnel. The pipe was capped to stop the leak (Whitacre, 2014b)."
2002 | 2002 Apr. | 6 | U | [6 empty] | No | NOT PROVIDED | NOT PROVIDED | !TT | 1 | OP | OP | Small |  |  | Small | JP-5 | taken out of service after a confirmed release |  |  | EPA-R09-UST-2015-0441-0559 (1).pdf | "Tank #6 taken out of service after a confirmed release (Sommer, 2002)."
2008 | 2008 Oct. | 2 | U | [7 empty] | ~200' - 210' |  | !TT |  | OP | OP | Small |  |  |  |  | API 653 Inspection |  |  | 2008 Oct 13_API 653 - Final Report_Red Hill Tank 2.pdf
2008 | 2008 Oct. | 2 | U | [7 empty] | ~200' - 210' |  | !TT |  | OP | OP | Small |  |  |  |  | API 653 Inspection |  |  | 2008 Oct 13_API 653 - Final Report_Red Hill Tank 2.pdf
2010 | 2010 Nov | 5 | U | [7 empty] | ~191' |  | !TT |  | OP | OP | Small |  |  |  |  | API 653 Inspection |  |  | RedHill_Tank05InspectionReport_18NOV10.pdf
2014 | 2014 Jan. 13 | 5 | V |  | 27000 |  |  |  |  | No | NOT PROVIDED | Multiple | !TT | 1 | TIR | RTS | Small | 27000 |  | Small | JP-5 | fuel loss | Fuel transferred to other tanks | After inspection (tests) | EPA-R09-UST-2015-0441-0559 (1).pdf red-hill-aoc-press-release (1).pdf Pearl Harbor Tank 0105 AFHE findings_02_6_2014_chronology.pdf RH_CompUnverLeakHistories_DEC17.xlsx | "Tank #5 back in service after routine scheduled maintenance, including cleaning, inspecting, and repairing multiple sites within the tank (US EPA and Hawaii DOH, 2015a)." (Dec 2014) "Tank #5 fuel loss estimated as approximately 27,000 gallons in written notification to Hawaii DOH (US EPA and Hawaii DOH, 2015a). Navy increases tank monitoring frequency (US EPA and Hawaii DOH, 2015a)." (Jan 2014)
| Years | Incidents | [15 empty] | Total release (Gallons) | Small Release (<2gpm) | 35 | [6 empty] | Tank 10 events |  |  |  | Tank 7 events
Total: | 75 | 61 |  |  | 120973 |  | 52360.095 | [10 empty] | 150050 | Large Release (>2gpm) | 0 | [6 empty] | gal per day | days | gallons leaked |  | gal per day | days | gallons leaked | gpm
Per Year: |  | 0.81333 | [15 empty] | 2000.6667 | [8 empty] | 13.3 | 29 | 385.7 |  | 609 | 4 | 2436 | 0.42292
[27 empty] | 12.8 | 24 | 307.2 |  | 334 | 5 | 1670 | 0.23194
[27 empty] | 2.4 | 38 | 91.2 |  | 208 | 7 | 1456 | 0.14444
|  | Summary | [24 empty] | 4.7 | 57 | 267.9 |  | 12.7 | 31 | 393.7 | 0.0088194
|  |  | Incidents | Notes | [22 empty] | 1206 | 2 | 2412 |  | 12 | 24 | 288 | 0.0083333
|  | Total Incidents | 65 | All incidents, excluding back seepage, and found during maintenance | [8 empty] | 32 | 14 | 12 | [11 empty] | 693 | 2 | 1386 |  | 2.6 | 20 | 52 | 0.0018056
|  | Total Verified | 47 | All incidents from the verfied Navy list. | [8 empty] | 29 | [13 empty] | 15 | 11 | 165 |  | 3.1 | 56 | 173.6 | 0.0021528
|  | Total Unverified (Included) | 9 | Incidents from the unverified history files that were not corroborated by the Navy verified list. | [23 empty] | sum = | 5015 |  |  | sum= | 6469.3 | total gallons leaked
|  | Exclusions | [29 empty] | total days = |  | 147 | days
|  | Maintenance, Leak Test with Water | 10 | Due to incidents during maintenance, back seapage. Five Leak Incidents during test that included water. | [22 empty] | 7/22/1980 to 1/10/1981 |  |  | 4/11/1980 to 7/22/1980
|  | Filters | [24 empty] | 8 | days |  | 19 |  | 2/20/1980 to 7/20/1980
|  | TellTale | 25 | Leak incidents in the TellTale, during operation. | [22 empty] | 31 |  |  | 31 | 2.6 | 150 | 390
|  | Incidents w.o. Tell-Tale | 18 | Incidents without the tell-tale and includes occurrences during leak test. Small (<2 gpm) releases w.o. Tell-Tale | [22 empty] | 30 |  |  | 31 | 609 | 150 | 91350
|  | RTS | 12 | Leaks detected during a RTS | [22 empty] | 31 |  |  | 22
[27 empty] | 30 |  |  | 103
31
| Tank 1 | 21 | [24 empty] | 10
| Tank 2 | 5 | [24 empty] | 3
| Tank 3 | 1 | [24 empty] | 10
| Tank 4 | 0 | [24 empty] | 184 | sum
| Tank 5 | 5 | [25 empty] | total days = |  | 287
| Tank 6 | 2
| Tank 7 | 3
| Tank 8 | 0
| Tank 9 | 3
| Tank 10 | 4
| Tank 11 | 1
| Tank 12 | 2
| Tank 13 | 2
| Tank 14 | 1
| Tank 15 | 1
| Tank 16 | 6
| Tank 17 | 3
| Tank 18 | 0
| Tank 19 | 1
| Tank 20 | 0
61

## All_Tanks_RH
Tanks: | 20
Tank 1 - 20 Releases | [12 empty] | Source
Tank | Start of Service Year | End of Service Year | Work on TellTale | Telltale Work Outage (Yrs) | TIRM & Repairs Outage (Yrs) | # of Outages / RTS | Tank Years | Small < 2 gpm |  |  |  |  | The outage periods and number of outages are detailed in the: "ReturnToService_021218.XLSX" file.
[8 empty] | wo Telltale |  | w Telltale
[8 empty] | # | λ /yr | # | λ /yr
1 | 1943 | 2005 | (1978/84) | 1 | 15.6252 | 10 | 45.3748 | 6 | 0.13223 | 9 | 0.19835
2 | 1943 | 2017 | (1978/84) | 1 | 4.2572 | 6 | 68.7428 | 2 | 0.029094 | 2 | 0.029094 | 2008 API 653 TRIM report indicates 2 holes that should be detected in the future. 0.018" and 1/2" holes. Please see "HolesDetectedDuringInspection_071918.xlsx" work book.
3 | 1943 | 2017 |  |  | 2.2818 | 4 | 71.7182 | 1 | 0.013943 | 0 | 0
4 | 1943 | 2017 |  |  | 2.0246 | 2 | 71.9754 | 0 | 0 | 0 | 0
5 | 1943 | 2017 | (1971/73) (1978/84) | 2 | 7.4063 | 6 | 64.5937 | 1 | 0.015481 | 3 | 0.046444 | 2010 API 653 TRIM report indicates 1 hole that should be detected in the future. 1/4" holes. Please see "HolesDetectedDuringInspection_071918.xlsx" work book.
6 | 1943 | 2017 | 1964 (1971/73) | 2 | 7.8468 | 8 | 64.1532 | 1 | 0.015588 | 1 | 0.015588
7 | 1943 | 2017 | (1978/84) | 1 | 3.5732 | 6 | 69.4268 | 0 | 0 | 2 | 0.028807
8 | 1943 | 2017 | (1978/84) | 1 | 2.3748 | 4 | 70.6252 | 0 | 0 | 0 | 0
9 | 1943 | 2017 | (1978/84) | 1 | 2.0547 | 5 | 70.9453 | 1 | 0.014095 | 1 | 0.014095
10 | 1943 | 2017 | (1978/84) | 1 | 8.2025 | 7 | 64.7975 | 1 | 0.015433 | 1 | 0.015433
11 | 1943 | 2017 |  |  | 2.9001 | 3 | 71.0999 | 1 | 0.014065 | 0 | 0
12 | 1943 | 2017 | (1971/73) (1978/84) | 2 | 7.5294 | 6 | 64.4706 | 0 | 0 | 0 | 0
13 | 1943 | 2017 | (1978/84) | 1 | 7.99 | 6 | 65.01 | 1 | 0.015382 | 0 | 0
14 | 1943 | 2017 |  |  | 3.08 | 5 | 70.92 | 1 | 0.0141 | 0 | 0
15 | 1943 | 2017 | 1981 | 1 | 5.2066 | 5 | 67.7934 | 0 | 0 | 0 | 0
16 | 1943 | 2017 | 1976 | 1 | 4.6047 | 8 | 68.3953 | 1 | 0.014621 | 3 | 0.043863
17 | 1943 | 2017 | (1960/63) (1978/84) | 2 | 1.67 | 6 | 70.33 | 1 | 0.014219 | 2 | 0.028437
18 | 1943 | 2017 | (1960/63) (1978/84) | 2 | 0.98495 | 5 | 71.015 | 0 | 0 | 0 | 0
19 | 1943 | 1998 | (1960/63) | 1 | 20.736 | 7 | 33.264 | 0 | 0 | 1 | 0.030063
20 | 1943 | 2017 | (1960/63) (1978/84) | 2 | 1.0014 | 4 | 70.9986 | 0 | 0 | 0 | 0
Total: |  |  | 22 |  |  | 113 | 1315.6499 | 18 | 0.30825 | 25 | 0.45017
Mean / yr: | [7 empty] | 0.013681 | 0.015413 | 0.019002 | 0.022509
1 Incident / n Yrs | [7 empty] | 73.0917 | 64.8817 | 52.626 | 44.4275
Tank 1 - 20 Releases -- Large > 2 gpm
RM DIST. | Distribution Type | Events | Alpha | Beta | λ /yr | 1 Incident / n Yrs | Median | 5th | 95th | Range Factor | Source
RHLALL | Gamma Non-Informative Prior | 0 | 0.5 | 1315.6499 | 0.000359 | 2785.5153 | 0.000148 | 1.19e-06 | 1270 | 32.6 | Red Hill
NAVYL | Gamma Non-Informative Prior | 0 | 0.5 | 7050 | 7.13e-05 | 14025.2454 | 2.94e-05 | 2.36e-07 | 0.000252 | 32.6 | Navy Bulk Tank Spill Releases Data
Probability of a Release Incident after a TRIM
# releases | # TRIMs | Probability
15 | 113 | 0.13274

## ALL_Trend
|  | Inc. Count | 10 Years | 15 Years | 25 years | Decades | incidents
1 | 1944 | 0 |  |  |  | 1944-1953 | 8
2 | 1945 | 0 |  |  |  | 1954-1963 | 3
3 | 1946 | 0 |  |  |  | 1964-1973 | 20
4 | 1947 | 2 |  |  |  | 1974-1983 | 23
5 | 1948 | 1 |  |  |  | 1984-1993 | 0
6 | 1949 | 3 |  |  |  | 1994-2003 | 3
7 | 1950 | 0 |  |  |  | 2004-2013 | 3
8 | 1951 | 0 |  |  |  | 2014-2017 | 1
9 | 1952 | 1
10 | 1953 | 1 | 8 |  |  | 15 Years
11 | 1954 | 2 |  |  |  | 1944-1958 | 11
12 | 1955 | 0 |  |  |  | 1959-1973 | 20
13 | 1956 | 0 |  |  |  | 1974-1988 | 23
14 | 1957 | 0 |  |  |  | 1989-2003 | 3
15 | 1958 | 1 |  | 11 |  | 2004-2017 | 4
16 | 1959 | 0
17 | 1960 | 0 |  |  |  | 25 Years
18 | 1961 | 0 |  |  |  | 1944-1968 | 21
19 | 1962 | 0 |  |  |  | 1969-1993 | 33
20 | 1963 | 0 | 3 |  |  | 1994-2017 | 7
21 | 1964 | 5
22 | 1965 | 3
23 | 1966 | 1
24 | 1967 | 1
25 | 1968 | 0 |  |  | 21
26 | 1969 | 1
27 | 1970 | 1
28 | 1971 | 2
29 | 1972 | 2
30 | 1973 | 4 | 20 | 20
31 | 1974 | 0
32 | 1975 | 2
33 | 1976 | 2
34 | 1977 | 1
35 | 1978 | 4
36 | 1979 | 0
37 | 1980 | 3
38 | 1981 | 7
39 | 1982 | 3
40 | 1983 | 1 | 23
41 | 1984 | 0
42 | 1985 | 0
43 | 1986 | 0
44 | 1987 | 0
45 | 1988 | 0 |  | 23
46 | 1989 | 0
47 | 1990 | 0
48 | 1991 | 0
49 | 1992 | 0
50 | 1993 | 0 | 0 |  | 33
51 | 1994 | 0
52 | 1995 | 0
53 | 1996 | 0
54 | 1997 | 0
55 | 1998 | 1
56 | 1999 | 1
57 | 2000 | 0
58 | 2001 | 0
59 | 2002 | 1
60 | 2003 | 0 | 3 | 3
61 | 2004 | 0
62 | 2005 | 0
63 | 2006 | 0
64 | 2007 | 0
65 | 2008 | 2
66 | 2009 | 0
67 | 2010 | 1
68 | 2011 | 0
69 | 2012 | 0
70 | 2013 | 0 | 3
71 | 2014 | 1
72 | 2015 | 0
73 | 2016 | 0
74 | 2017 | 0 | 1 | 4 | 7
61

## Trend_Operational
|  | Inc. Count | 10 Years | 15 Years | 25 years | Decades | incidents
1 | 1944 | 0 |  |  |  | 1944-1953 | 2
2 | 1945 | 0 |  |  |  | 1954-1963 | 0
3 | 1946 | 0 |  |  |  | 1964-1973 | 5
4 | 1947 | 0 |  |  |  | 1974-1983 | 6
5 | 1948 | 0 |  |  |  | 1984-1993 | 0
6 | 1949 | 2 |  |  |  | 1994-2003 | 2
7 | 1950 | 0 |  |  |  | 2004-2013 | 3
8 | 1951 | 0 |  |  |  | 2014-2017 | 0
9 | 1952 | 0
10 | 1953 | 0 | 2 |  |  | 15 Years
11 | 1954 | 0 |  |  |  | 1944-1958 | 2
12 | 1955 | 0 |  |  |  | 1959-1973 | 5
13 | 1956 | 0 |  |  |  | 1974-1988 | 6
14 | 1957 | 0 |  |  |  | 1989-2003 | 2
15 | 1958 | 0 |  | 2 |  | 2004-2017 | 3
16 | 1959 | 0
17 | 1960 | 0 |  |  |  | 25 Years
18 | 1961 | 0 |  |  |  | 1944-1968 | 2
19 | 1962 | 0 |  |  |  | 1969-1993 | 11
20 | 1963 | 0 | 0 |  |  | 1994-2017 | 5
21 | 1964 | 0
22 | 1965 | 0
23 | 1966 | 0
24 | 1967 | 0
25 | 1968 | 0 |  |  | 2
26 | 1969 | 0
27 | 1970 | 1
28 | 1971 | 2
29 | 1972 | 1
30 | 1973 | 1 | 5 | 5
31 | 1974 | 0
32 | 1975 | 1
33 | 1976 | 1
34 | 1977 | 0
35 | 1978 | 0
36 | 1979 | 0
37 | 1980 | 2
38 | 1981 | 0
39 | 1982 | 2
40 | 1983 | 0 | 6
41 | 1984 | 0
42 | 1985 | 0
43 | 1986 | 0
44 | 1987 | 0
45 | 1988 | 0 |  | 6
46 | 1989 | 0
47 | 1990 | 0
48 | 1991 | 0
49 | 1992 | 0
50 | 1993 | 0 | 0 |  | 11
51 | 1994 | 0
52 | 1995 | 0
53 | 1996 | 0
54 | 1997 | 0
55 | 1998 | 1
56 | 1999 | 0
57 | 2000 | 0
58 | 2001 | 0
59 | 2002 | 1
60 | 2003 | 0 | 2 | 2
61 | 2004 | 0
62 | 2005 | 0
63 | 2006 | 0
64 | 2007 | 0
65 | 2008 | 2
66 | 2009 | 0
67 | 2010 | 1
68 | 2011 | 0
69 | 2012 | 0
70 | 2013 | 0 | 3
71 | 2014 | 0
72 | 2015 | 0
73 | 2016 | 0
74 | 2017 | 0 | 0 | 3 | 5
18

## RTS_Trend
RTS Count
1 | 1944 | 0
2 | 1945 | 0
3 | 1946 | 0
4 | 1947 | 0
5 | 1948 | 0
6 | 1949 | 0
7 | 1950 | 0
8 | 1951 | 0
9 | 1952 | 0
10 | 1953 | 0
11 | 1954 | 0
12 | 1955 | 0
13 | 1956 | 0
14 | 1957 | 0
15 | 1958 | 0
16 | 1959 | 0
17 | 1960 | 0
18 | 1961 | 0
19 | 1962 | 0
20 | 1963 | 0
21 | 1964 | 0
22 | 1965 | 0
23 | 1966 | 0
24 | 1967 | 0
25 | 1968 | 0
26 | 1969 | 0
27 | 1970 | 0
28 | 1971 | 0
29 | 1972 | 0
30 | 1973 | 0
31 | 1974 | 0
32 | 1975 | 0
33 | 1976 | 0
34 | 1977 | 0
35 | 1978 | 1
36 | 1979 | 0
37 | 1980 | 1
38 | 1981 | 7
39 | 1982 | 1
40 | 1983 | 1
41 | 1984 | 0
42 | 1985 | 0
43 | 1986 | 0
44 | 1987 | 0
45 | 1988 | 0
46 | 1989 | 0
47 | 1990 | 0
48 | 1991 | 0
49 | 1992 | 0
50 | 1993 | 0
51 | 1994 | 0
52 | 1995 | 0
53 | 1996 | 0
54 | 1997 | 0
55 | 1998 | 0
56 | 1999 | 0
57 | 2000 | 0
58 | 2001 | 0
59 | 2002 | 0
60 | 2003 | 0
61 | 2004 | 0
62 | 2005 | 0
63 | 2006 | 0
64 | 2007 | 0
65 | 2008 | 0
66 | 2009 | 0
67 | 2010 | 0
68 | 2011 | 0
69 | 2012 | 0
70 | 2013 | 0
71 | 2014 | 1
72 | 2015 | 0
73 | 2016 | 0
74 | 2017 | 0
12

## TT_Trend
TT-OP Count
1 | 1944 | 0
2 | 1945 | 0
3 | 1946 | 0
4 | 1947 | 2
5 | 1948 | 1
6 | 1949 | 1
7 | 1950 | 0
8 | 1951 | 0
9 | 1952 | 1
10 | 1953 | 0
11 | 1954 | 1
12 | 1955 | 0
13 | 1956 | 0
14 | 1957 | 0
15 | 1958 | 1
16 | 1959 | 0
17 | 1960 | 0
18 | 1961 | 0
19 | 1962 | 0
20 | 1963 | 0
21 | 1964 | 5
22 | 1965 | 2
23 | 1966 | 0
24 | 1967 | 0
25 | 1968 | 0
26 | 1969 | 1
27 | 1970 | 0
28 | 1971 | 0
29 | 1972 | 1
30 | 1973 | 2
31 | 1974 | 0
32 | 1975 | 1
33 | 1976 | 1
34 | 1977 | 1
35 | 1978 | 3
36 | 1979 | 0
37 | 1980 | 0
38 | 1981 | 0
39 | 1982 | 0
40 | 1983 | 0
41 | 1984 | 0
42 | 1985 | 0
43 | 1986 | 0
44 | 1987 | 0
45 | 1988 | 0
46 | 1989 | 0
47 | 1990 | 0
48 | 1991 | 0
49 | 1992 | 0
50 | 1993 | 0
51 | 1994 | 0
52 | 1995 | 0
53 | 1996 | 0
54 | 1997 | 0
55 | 1998 | 0
56 | 1999 | 1
57 | 2000 | 0
58 | 2001 | 0
59 | 2002 | 0
60 | 2003 | 0
61 | 2004 | 0
62 | 2005 | 0
63 | 2006 | 0
64 | 2007 | 0
65 | 2008 | 0
66 | 2009 | 0
67 | 2010 | 0
68 | 2011 | 0
69 | 2012 | 0
70 | 2013 | 0
71 | 2014 | 0
72 | 2015 | 0
73 | 2016 | 0
74 | 2017 | 0
25

## OP_Trend
OP - No TT Count
1 | 1944 | 0
2 | 1945 | 0
3 | 1946 | 0
4 | 1947 | 0
5 | 1948 | 0
6 | 1949 | 2
7 | 1950 | 0
8 | 1951 | 0
9 | 1952 | 0
10 | 1953 | 0
11 | 1954 | 0
12 | 1955 | 0
13 | 1956 | 0
14 | 1957 | 0
15 | 1958 | 0
16 | 1959 | 0
17 | 1960 | 0
18 | 1961 | 0
19 | 1962 | 0
20 | 1963 | 0
21 | 1964 | 0
22 | 1965 | 0
23 | 1966 | 0
24 | 1967 | 0
25 | 1968 | 0
26 | 1969 | 0
27 | 1970 | 1
28 | 1971 | 2
29 | 1972 | 1
30 | 1973 | 1
31 | 1974 | 0
32 | 1975 | 1
33 | 1976 | 1
34 | 1977 | 0
35 | 1978 | 0
36 | 1979 | 0
37 | 1980 | 2
38 | 1981 | 0
39 | 1982 | 2
40 | 1983 | 0
41 | 1984 | 0
42 | 1985 | 0
43 | 1986 | 0
44 | 1987 | 0
45 | 1988 | 0
46 | 1989 | 0
47 | 1990 | 0
48 | 1991 | 0
49 | 1992 | 0
50 | 1993 | 0
51 | 1994 | 0
52 | 1995 | 0
53 | 1996 | 0
54 | 1997 | 0
55 | 1998 | 1
56 | 1999 | 0
57 | 2000 | 0
58 | 2001 | 0
59 | 2002 | 1
60 | 2003 | 0
61 | 2004 | 0
62 | 2005 | 0
63 | 2006 | 0
64 | 2007 | 0
65 | 2008 | 2
66 | 2009 | 0
67 | 2010 | 1
68 | 2011 | 0
69 | 2012 | 0
70 | 2013 | 0
71 | 2014 | 0
72 | 2015 | 0
73 | 2016 | 0
74 | 2017 | 0
18

## NavyBulkTank_SpillReleaseData
Tank Location | Tank No. | Nominal Capacity (gal) | Nominal Capacity (Bbl) | Product | AST/UST | Const Yr | Tank Yrs | Shape & Orientation | Tank Dimensions (Diameter x Height) | Tank Material | Releases? | Release (Small <2 gpm Larg > 2gpm) | Date of Release | Reason for Release(s) | Misc Notes
Sasebo‐Akasaki | 2190‐2 | 27846 | 663 | lube Oil | AST | 2004 | 13 | Horizontal Cylindrical | 11.5' (D) x 37' (L) | Double‐walled, Steel, welded
Sasebo‐Akasaki | 2190‐1 | 27846 | 663 | lube Oil | AST | 2004 | 13 | Horizontal Cylindrical | 11.5' (D) x 37' (L) | Double‐walled, Steel, welded
Sasebo‐Akasaki | AS‐5 (Old: 6400501) | 792036 | 18858 | Slop | AST | 1973 | 44 | Vertical Cylindrical | 60' x 40' | Steel, welded (field constructed)
Sasebo‐Akasaki | A‐1 (Old: 6400577) | 576366 | 13723 | MOGAS | AST | 1995 | 22 | Vertical Cylindrical | 51' x 45' | Steel, welded (field constructed)
Sasebo‐Akasaki | A‐2 (Old: 6400578) | 6299958 | 149999 | F‐76 | AST | 1995 | 22 | Vertical Cylindrical | 133' x 65' | Steel, welded (field constructed)
Sasebo‐Akasaki | A‐3 (Old: 6400579) | 6299622 | 149991 | JP‐5 | AST | 1995 | 22 | Vertical Cylindrical | 133' x 65' | Steel, welded (field constructed) | 3 gal;20 gal | Small | 4/25/1994; 05/11/1994 | Spill from cargo hose which was used to transfer from AS‐5 to AS‐3 from both events.
Sasebo‐Akasaki | A‐4 (Old: 6400591) | 5100228 | 121434 | F‐76 | UST | 1998 | 19 | Vertical Cylindrical | 155' x 40' | Welded steel primary tank encase in concrete
Sasebo‐Akasaki | A‐5 (Old: 6400592) | 4952850 | 117925 | JP‐5 | UST | 1998 | 19 | Vertical Cylindrical | 155' x 40' | Welded steel primary tank encase in concrete
Sasebo‐Akasaki | A‐6 (Old: 6400598) | 5097708 | 121374 | F‐76 | UST | 2002 | 15 | Vertical Cylindrical | 155' x 40' | Welded steel primary tank encase in concrete
Sasebo‐Akasaki | A‐7 (Old: 6400599) | 5106318 | 121579 | JP‐5 | UST | 2002 | 15 | Vertical Cylindrical | 155' x 40' | Welded steel primary tank encase in concrete
Sasebo‐Akasaki | A‐8 (Old: 6400580) | 303996 | 7238 | JP‐5 | AST | 1995 | 22 | Vertical Cylindrical | 38' x 38.5' | Steel, welded (field constructed)
Sasebo‐Akasaki | A‐9 (Old: 6400581) | 305130 | 7265 | F‐76 | AST | 1995 | 22 | Vertical Cylindrical | 38' x 38.5' | Steel, welded (field constructed)
Sasebo‐Akasaki | A‐10 (Old: 6400582) | 281820 | 6710 | MOGAS | AST | 1995 | 22 | Vertical Cylindrical | 38' x 38.5' | Steel, welded (field constructed)
Sasebo‐Akasaki | A‐12 (Old: 6400541) | 13820268 | 329054 | JP‐5 | UST | 1985 | 32 | Vertical Cylindrical | 236' x 46' | Double wall (cofferdam); Welded steel primary tank encase in concrete
Sasebo‐Iorizaki | I‐1 (Formerly 6300799) | 9659454 | 229987 | F‐76 | UST | 1987 | 30 | Square | 136.7' (W) x 439.8' (L) x 23.3' (H) | Double wall (cofferdam); Welded steel primary tank encase in concrete |  |  |  |  | **New constr year dates after the secondary containment was put into these tanks.
Sasebo‐Iorizaki | I‐2 (Formerly 6300803) | 14607852 | 347806 | F‐76 | UST | 1987 | 30 | Square | 190.3' (W) x 426.7' (L) x 27.3' (H) | Double wall (cofferdam); Welded steel primary tank encase in concrete |  |  |  |  | UST has concrete coffer dam secondary cont.
Sasebo‐Iorizaki | I‐3 (Formerly 6300772) | 12801852 | 304806 | JP‐5 | UST | 1984 | 33 | Square | 190.7' (W) x 426.7' (L) x 21.7' (H) | Double wall (cofferdam); Welded steel primary tank encase in concrete |  |  |  |  | UST has concrete coffer dam secondary cont.
Sasebo‐Iorizaki | I‐4 (Formerly 6300773) | 17678052 | 420906 | JP‐5 | UST | 1982 | 35 | Square | 279.4' (W) x 397.2' (L) x 21.8' (H) | Double wall (cofferdam); Welded steel primary tank encase in concrete |  |  |  |  | **New constr year dates after the secondary containment was put into these tanks.
Sasebo‐Iorizaki | I‐5 (Formerly M705) | 392868 | 9354 | F‐76 | AST | 1953 | 64 | Vertical Cylindrical | 55' x 24' | Steel, welded (field constructed) |  |  |  |  | Site took tank of service on 2 /15/2016
Sasebo‐Yokose | YOK Tank Y‐1 | 15615936 | 371808 | F‐76 | UST | 1984 | 33 | Vertical Cylindrical | 278.5' x 36.8' | Double wall (cofferdam); Welded steel primary tank encase in concrete |  |  |  |  | UST has concrete coffer dam secondary cont.
Sasebo‐Yokose | YOK Tank Y‐2 | 15614928 | 371784 | F‐76 | UST | 1985 | 32 | Vertical Cylindrical | 278.5' x 36.7' | Double wall (cofferdam); Welded steel | Release of 30k gal in 2005; since this is a double walled tank, all released fuel was | Small |  |  | UST has concrete coffer dam secondary cont.
Sasebo‐Yokose | YOK Tank Y‐3 | 15638658 | 372349 | F‐76 | UST | 1988 | 29 | Vertical Cylindrical | 278.5' x 36.8' | Double wall (cofferdam); Welded steel primary tank encase in concrete |  |  |  |  | UST has concrete coffer dam secondary cont.
Sasebo‐Yokose | YOK Tank Y‐4 | 15615264 | 371792 | JP‐5 | UST | 1986 | 31 | Vertical Cylindrical | 278.5' x 36.7' | Double wall (cofferdam); Welded steel primary tank encase in concrete
Sasebo‐Yokose | YOK Tank Y‐5 | 15647856 | 372568 | JP‐5 | UST | 1989 | 28 | Vertical Cylindrical | 278.5' x 36.7' | Double wall (cofferdam); Welded steel primary tank encase in concrete
Sasebo‐Yokose | YOK Tank Y‐6 | 15646008 | 372524 | JP‐5 | UST | 1990 | 27 | Vertical Cylindrical | 278.5' x 36.8' | Double wall (cofferdam); Welded steel primary tank encase in concrete |  |  |  |  | UST has concrete coffer dam secondary cont. 2/9/2012
Sasebo‐Yokose | YOK Tank Y‐7 | 15646176 | 372528 | JP‐5 | UST | 1991 | 26 | Vertical Cylindrical | 278.5' x 36.8' | Double wall (cofferdam); Welded steel primary tank encase in concrete
Sasebo‐Yokose | YOK Tank Y‐8 | 4194246 | 99863 | JP‐5 | UST | 1994 | 23 | Vertical Cylindrical | 146.3' x 38.9' | Welded steel primary tank encase in concrete |  |  |  |  | RTS 7/15/2015
Sasebo‐Yokose | YOK Tank Y‐9 | 399336 | 9508 | F‐76 | AST | 1974 | 43 | Vertical Cylindrical | 55' x 25.4' | Steel, welded (field constructed) |  |  |  |  | Formerly Tank YS‐3
Sasebo‐Yokose | YOK Tank Y‐10 | 805476 | 19178 | F‐76 | AST | 1973 | 44 | Vertical Cylindrical | 60' x 40' | Steel, welded (field constructed) |  |  |  |  | Formerly Tank YS‐5
Hakozaki | 101 (Formerly 33) | 8387400 | 199700 | JP‐8 | UST | 1937 | 80 | Vertical Cylindrical | 125' x 95' | Steel & Coated
Hakozaki | 102 | 13116096 | 312288 | JP‐5 | UST | 2005 | 12 | Vertical Cylindrical | 170' x 83' | Steel & Coated
Hakozaki | 103 (Formerly 36) | 8552964 | 203642 | JP‐8 | UST | 1937 | 80 | Vertical Cylindrical | 125' x 95' | Steel & Coated | F‐76 900 gals | Small | 31‐Mar‐86 | CRACKS | Double bottom installed in 1987, RTS 5/29/2015
Hakozaki | 104 (Formerly 37) | 8547966 | 203523 | F‐76 | UST | 1936 | 81 | Vertical Cylindrical | 125' x 95' | Steel & Coated | JP‐5 NO RECORD | Small | 9‐Jan‐74 | Riveted joint | Double bottom installed in 1985
Hakozaki | 105 (Formerly 8600408 | 8676696 | 206588 | F‐76 | UST | 2002 | 15 | Vertical Cylindrical | 156' x 78' | Steel & Coated
Hakozaki | 106 (Formerly 40) | 8789256 | 209268 | F‐76 | UST | 1936 | 81 | Vertical Cylindrical | 125' x 95' | Steel & Coated | F‐76 1,260 GALS | Small | 12‐Aug‐85 | Holes | Major renovations in 1980
Hakozaki | 107 (Formerly 43) | 8124774 | 193447 | JP‐5 | UST | 1936 | 81 | Vertical Cylindrical | 125' x 95' | Steel & Coated | JP‐5 1,97 GALS | Small | 21‐Apr‐82 | PIN HOLES IN LINING | Major renovations in 1991
Hakozaki | 108 (Formerly 44) | 5296788 | 126114 | F‐76 | UST | 1927 | 90 | Vertical Cylindrical | 104' x 93' | Steel & Coated | F‐76 360 GALS | Small | 21‐May‐81 | CRACKS IN WELDED SEAMS & LINING | Not suitable for service, repaired
Hakozaki | 109 (Formerly 45) | 6064170 | 144385 | F‐76 | UST | 1927 | 90 | Vertical Cylindrical | 104' x 93' | Steel & Coated |  |  |  |  | Major renovations in 1985
Hakozaki | 110 (Formerly 46) | 6067068 | 144454 | F‐76 | UST | 1927 | 90 | Vertical Cylindrical | 104' x 93' | Steel & Coated | JP‐4 NO RECORD | Small | 25‐Aug‐74 | CRACKS (DURING FILL TEST )
Hakozaki | 112 (Formerly 162) | 5561976 | 132428 | JP‐5 | UST | 1928 | 89 | Vertical Cylindrical | 105' x 89' | Steel & Coated |  |  |  |  | Double bottom installed in 1987
Hakozaki | 113 (Formerly 161) | 5573064 | 132692 | JP‐5 | UST | 1928 | 89 | Vertical Cylindrical | 105' x 88' | Steel & Coated, Courses 1‐5, 17 welded. Courses 5‐16 riveted |  |  |  |  | Double bottom installed in 1987.
Hakozaki | 114 (Formerly 157) | 1656354 | 39437 | MOGAS | AST | 1939 | 78 | Vertical Cylindrical | 90' x 37'
Hakozaki | 115 (Formerly 155) | 1652448 | 39344 | MOGAS | AST | 1939 | 78 | Vertical Cylindrical | 90' x 37'
Hakozaki | 117 (Formerly 8600337 | 831600 | 19800 | F‐76 | AST | 1975 | 42 | Vertical Cylindrical | 60' x 40'
Hakozaki | 118 (Formerly 8600336 | 75600 | 1800 | Oily Water | AST | 1975 | 42 | Vertical Cylindrical | 24' x 23' | [5 empty] | Product: Bottom Water, estimated RTS 10/9/2015
Hakozaki | 4306 | 5000 | 119 | MOGAS | UST | 1993 | 24 | Horizontal Cylindrical | 6.2' x 24' | [5 empty] | to be replaced by FY20 MILCON, CFAY Gas Station.
Hakozaki | 4306 | 5000 | 119 | Diesel | UST | 1993 | 24 | Horizontal Cylindrical | 6.2' x 24' | [5 empty] | to be replaced by FY20 MILCON, CFAY Gas Station.
Hakozaki | 4306 | 5000 | 119 | Kerosene | UST | 1993 | 24 | Horizontal Cylindrical | 6.2' x 24' | [5 empty] | to be replaced by FY20 MILCON, CFAY Gas Station.
Hakozaki | 4306 | 5000 | 119 | MOGAS | UST | 1993 | 24 | Hrizontal Cylindrical | 6.2' x 24' | [5 empty] | to be replaced by FY20 MILCON, CFAY Gas Station.
Hakozaki | 4306 | 5000 | 119 | Diesel | UST | 1993 | 24 | Hrizontal Cylindrical | 6.2' x 24' | [5 empty] | to be replaced by FY20 MILCON, CFAY Gas Station.
Hakozaki | 48 (Formerly 25) | 58800 | 1400 | Oily Water | AST | 1934 | 83 | Vertical Cylindrical | 20' x 30' | [5 empty] | expected RTS 10/9/2015
Hakozaki | 49 (Formerly 27) | 58800 | 1400 | Oily Water | AST | 1934 | 83 | Vertical Cylindrical | 20' x 30'
Hakozaki | 50 (Formerly 29) | 58800 | 1400 | Oily Water | AST | 1934 | 83 | Vertical Cylindrical | 23' x 30' | [5 empty] | expected RTS 10/9/2015
Hakozaki | 51 (Formerly 21) | 142338 | 3389 | Water | AST | 1938 | 79 | Vertical Cylindrical | 30' x 30'
Hakozaki | 52 (Formerly 22) | 142380 | 3390 | Water | AST | 1938 | 79 | Vertical Cylindrical | 30' x 30'
Hakozaki | 53 (Formerly 23) | 126000 | 3000 | MOGAS | AST | 1938 | 79 | Vertical Cylindrical | 30' x 30'
Hakozaki | 54 (Formerly 24) | 126000 | 3000 | MOGAS | AST | 1938 | 79 | Vertical Cylindrical | 30' x 30'
Hakozaki | 55 (Formerly 26) | 134400 | 3200 | JP‐5 | AST | 1938 | 79 | Vertical Cylindrical | 30' x 30'
Hakozaki | 56 (Formerly 28) | 134400 | 3200 | JP‐5 | AST | 1939 | 78 | Vertical Cylindrical | 30' x 30'
Hakozaki | 58 (Formerly 31) | 138600 | 3300 | F‐76 | AST | 1939 | 78 | Vertical Cylindrical | 30' x 30'
Hakozaki | 63 (Formerly 232) | 126000 | 3000 | F‐76 | AST | 1939 | 78 | Vertical Cylindrical | 33' x 24'
Hakozaki | 64 (Formerly 233) | 126000 | 3000 | F‐76 | AST | 1939 | 78 | Vertical Cylindrical | 33' x 24'
Hakozaki | 65 (Formerly 231) | 126000 | 3000 | F‐76 | AST | 1939 | 78 | Vertical Cylindrical | 33' x 24'
Hakozaki | 8600413 | 20001 | 476 | lube Oil | AST | 2003 | 14 | Horizontal split tank | 11' x 48'
Hakozaki | 8600414 | 10001 | 238 | lube Oil | AST | 2005 | 12 | Horizontal split tank | 11' x 48'
Hakozaki | 8600413 | 10001 | 238 | lube Oil | AST | 2003 | 14 | Horizontal split tank | 11' x 48'
Hakozaki | 8600414 | 20001 | 476 | lube Oil | AST | 2005 | 12 | Horizontal split tank | 11' x 48'
NB Guam | SAS Tank 1708A‐SV | 10000 | 238 | FSII | AST | 2013 | 4 | Horizontal Cylindrical | 10'6(D)x15'7"(L) | Stainless Steel | No |  |  |  | Source: FSII completion report April 2013.
NB Guam | SAS Tank 1708B‐SV | 8000 | 190 | FSII | AST | 2013 | 4 | Horizontal Cylindrical | 10' (D)x 13'7" (L) | Stainless Steel | No |  |  |  | Source: FSII completion report April 2013.
NB Guam | SAS Tank B1 | 840000 | 20000 | FOR | AST | 1952 | 65 | Vertical Cylindrical | 60' x 40' | API 650 Steel | No |  |  |  | Source: NBG SPCC Plan
NB Guam | SAS Tank B2 | 840000 | 20000 | FOR | AST | 1952 | 65 | Vertical Cylindrical | 60' x 40' | API 650 Steel | No |  |  |  | Source: NBG SPCC Plan
NB Guam | SAS Tank H2 | 84000 | 2000 | FOR | AST | 1952 | 65 | Vertical Cylindrical | 25' x 24' | API 650 Steel | No |  |  |  | Source: API 653 OCT 2016
NB Guam | SAS Tank L1 | 84000 | 2000 | FOR | AST | 1952 | 65 | Vertical Cylindrical | 25' x 24' | API 650 Steel | No |  |  |  | Source: API 653 OCT 2016
NB Guam | SAS Tank R1 | 21000 | 500 | FOR | AST | 1952 | 65 | Vertical Cylindrical | 15' x 16' | API 650 Steel | No |  |  |  | Source: API 653 JUN 2013
NB Guam | SAS Tank S1 | 420000 | 10000 | RME | AST | 1952 | 65 | Vertical Cylindrical | 45' x 40' | API 650 Steel | No |  |  |  | Source: API 653 OCT 2016
NB Guam | SAS Tank S2 | 210000 | 5000 | F‐76 | AST | 1952 | 65 | Vertical Cylindrical | 30' x 40' | API 650 Steel | No |  |  |  | Source: API 653 OCT 2016
NB Guam | SAS Tank S3 | 210000 | 5000 | JP‐8 | AST | 1952 | 65 | Vertical Cylindrical | 30' x 39'10" | API 650 Steel | No |  |  |  | Source: API 653 OCT 2016
NB Guam | SAS Tank S4 | 210000 | 5000 | JP‐5 | AST | 1952 | 65 | Vertical Cylindrical | 30' x 40' | API 650 Steel | No |  |  |  | Source: API 2012
NB Guam | SAS Tank S5 | 210000 | 5000 | JP‐8 | AST | 1952 | 65 | Vertical Cylindrical | 30' x 40' | API 650 Steel | No |  |  |  | Source: As Build DWG'
NB Guam | SAS Tank U1 | 2086266 | 49673 | JP‐5 | UST | 1952 | 65 | Vertical Cylindrical | 122' x 24' | API 650 Steel | No |  |  |  | Source: As Build DWG
NB Guam | SAS Tank U10 | 2086266 | 49673 | F‐76 | UST | 1952 | 65 | Vertical Cylindrical | 122' x 24' | API 650 Steel | No |  |  |  | Source: As Build DWG
NB Guam | SAS Tank U11 | 2086266 | 49673 | F‐76 | UST | 1952 | 65 | Vertical Cylindrical | 122' x 24' | API 650 Steel | No |  |  |  | Source: As Build DWG
NB Guam | SAS Tank U12 | 1995000 | 47500 | RME | UST | 1952 | 65 | Vertical Cylindrical | 122' x 24' | API 650 Steel | No |  |  |  | Source: As Build DWG
NB Guam | SAS Tank U13 | 2100000 | 50000 | RME | UST | 1952 | 65 | Vertical Cylindrical | 122' x 24' | API 650 Steel | No |  |  |  | Source: As Build DWG
NB Guam | SAS Tank U14 | 2100000 | 50000 | RME | UST | 1952 | 65 | Vertical Cylindrical | 122' x 24' | API 650 Steel | No |  |  |  | Source: As Build DWG
NB Guam | SAS Tank U15 | 2100000 | 50000 | RME | UST | 1952 | 65 | Vertical Cylindrical | 122' x 24' | API 650 Steel | No |  |  |  | Source: As Build DWG
NB Guam | SAS Tank U16 | 2100000 | 50000 | RME | UST | 1952 | 65 | Vertical Cylindrical | 122' x 24' | API 650 Steel | No |  |  |  | Source: As Build DWG
NB Guam | SAS Tank U17 | 2100000 | 50000 | JP‐8 | UST | 1954 | 63 | Vertical Cylindrical | 122' x 24' | API 650 Steel | No |  |  |  | Source: As Build DWG
NB Guam | SAS Tank U18 | 2100000 | 50000 | JP‐8 | UST | 1954 | 63 | Vertical Cylindrical | 122' x 24' | API 650 Steel | No |  |  |  | Source: As Build DWG
NB Guam | SAS Tank U19 | 2100000 | 50000 | JP‐8 | UST | 1957 | 60 | Vertical Cylindrical | 122' x 24' | API 650 Steel | No |  |  |  | Source: As Build DWG
NB Guam | SAS Tank U2 | 2085258 | 49649 | JP‐5 | UST | 1952 | 65 | Vertical Cylindrical | 122' x 24' | API 650 Steel | No |  |  |  | Source: As Build DWG
NB Guam | SAS Tank U20 | 2100000 | 50000 | JP‐5 | UST | 1957 | 60 | Vertical Cylindrical | 122' x 24' | API 650 Steel | No |  |  |  | Source: As Build DWG
NB Guam | SAS Tank U3 | 2100000 | 50000 | JP‐8 | UST | 1952 | 65 | Vertical Cylindrical | 122' x 24' | API 650 Steel | No |  |  |  | Source: As Build DWG
NB Guam | SAS Tank U4 | 2100000 | 50000 | JP‐8 | UST | 1952 | 65 | Vertical Cylindrical | 122' x 24' | API 650 Steel | No |  |  |  | Source: As Build DWG
NB Guam | SAS Tank U5 | 2087106 | 49693 | JP‐5 | UST | 1952 | 65 | Vertical Cylindrical | 122' x 24' | API 650 Steel | No |  |  |  | Source: As Build DWG
NB Guam | SAS Tank U6 | 2086350 | 49675 | JP‐5 | UST | 1952 | 65 | Vertical Cylindrical | 122' x 24' | API 650 Steel | No |  |  |  | Source: As Build DWG
NB Guam | SAS Tank U7 | 1995000 | 47500 | JP‐5 | UST | 1952 | 65 | Vertical Cylindrical | 122' x 24' | API 650 Steel | No |  |  |  | Source: As Build DWG
NB Guam | SAS Tank U8 | 2100000 | 50000 | JP‐5 | UST | 1952 | 65 | Vertical Cylindrical | 122' x 24' | API 650 Steel | No |  |  |  | Source: As Build DWG
NB Guam | SAS Tank U9 | 2087316 | 49698 | F‐76 | UST | 1952 | 65 | Vertical Cylindrical | 122' x 24' | API 650 Steel | Maybe | Small |  | As of 08‐31‐2017, no known source of sheen seen on 11‐09‐2016. Under investigation. | Source: As Build DWG
NB Guam | TEN Tank 28 | 2105544 | 50132 | F‐76 | UST | 1960 | 57 | Vertical Cylindrical | 122' x 24' | API 650 Steel | No |  |  |  | Source: As Build DWG
NB Guam | TEN Tank 29 | 2105628 | 50134 | F‐76 | UST | 1960 | 57 | Vertical Cylindrical | 122' x 24' | API 650 Steel | No |  |  |  | Source: As Build DWG
NB Guam | TEN Tank 31 | 2104788 | 50114 | F‐76 | UST | 1960 | 57 | Vertical Cylindrical | 122' x 24' | API 650 Steel | No |  |  |  | Source: As Build DWG
NB Guam | TEN Tank 33 | 3440304 | 81912 | F‐76 | UST | 1969 | 48 | Vertical Cylindrical | 134' x 32' | API 650 Steel | No |  |  |  | Source: As Build DWG
NB Guam | TEN Tank 34 | 3440640 | 81920 | F‐76 | UST | 1969 | 48 | Vertical Cylindrical | 134' x 32' | API 650 Steel | No |  |  |  | Source: As Build DWG
NB Guam | TEN Tank 35 | 3440304 | 81912 | F‐76 | UST | 1969 | 48 | Vertical Cylindrical | 134' x 32' | API 650 Steel | No |  |  |  | Source: As Build DWG
NB Guam | TEN Tank ST32 | 79800 | 1900 | FOR | AST | 1960 | 57 | Vertical Cylindrical | 25' x 24' | API 650 Steel | No |  |  |  | Source: API 653 OCT 2016
NB Guam | TEN Tank U30 | 2100000 | 50000 | F‐76 | UST | 1960 | 57 | Vertical Cylindrical | 122' x 24' | API 650 Steel | No
FLC Puget Sound | 115 | 42000 | 1000 | FOR | AST | 1941 | 76 | Vertical Cylindrical | 30' x 8' | Steel | No
FLC Puget Sound | 116 | 42000 | 1000 | FOR | AST | 1941 | 76 | Vertical Cylindrical | 30' x 8' | Steel | No
FLC Puget Sound | 14 | 105000 | 2500 | JP‐5 | UST | 1942 | 75 | Vertical Cylindrical | 35' x 15' | Concrete | No
FLC Puget Sound | 141 | 2100000 | 50000 | F‐24 | UST | 1952 | 65 | Vertical Cylindrical | 122' x 36' | Steel | No
FLC Puget Sound | 142 | 2100000 | 50000 | F‐24 | UST | 1952 | 65 | Vertical Cylindrical | 122' x 36' | Steel | No
FLC Puget Sound | 145 | 3360000 | 80000 | F‐24 | AST | 1955 | 62 | Vertical Cylindrical | 120' x 44' | Steel | No
FLC Puget Sound | 146 | 3360000 | 80000 | F‐24 | AST | 1955 | 62 | Vertical Cylindrical | 120' x 44' | Steel | No
FLC Puget Sound | 147 | 3360000 | 80000 | F‐24 | AST | 1955 | 62 | Vertical Cylindrical | 120' x 44' | Steel | No
FLC Puget Sound | 148 | 3360000 | 80000 | F‐24 | AST | 1955 | 62 | Vertical Cylindrical | 120' x 44' | Steel | No
FLC Puget Sound | 149 | 3360000 | 80000 | F‐24 | AST | 1955 | 62 | Vertical Cylindrical | 120' x 44' | Steel | No
FLC Puget Sound | 16 | 1134000 | 27000 | JP‐5 | UST | 1942 | 75 | Vertical Cylindrical | 100' x 20' | Concrete | No
FLC Puget Sound | 17 | 1134000 | 27000 | JP‐5 | UST | 1942 | 75 | Vertical Cylindrical | 100' x 20' | Concrete | No
FLC Puget Sound | 179 | 210000 | 5000 | Slop | AST | 1977 | 40 | Vertical Cylindrical | 30' x 41' | Steel | No
FLC Puget Sound | 18 | 1134000 | 27000 | JP‐5 | UST | 1942 | 75 | Vertical Cylindrical | 100' x 20' | Concrete | No
FLC Puget Sound | 180 | 1134000 | 27000 | Slop | AST | 1977 | 40 | Vertical Cylindrical | 70' x 41' | Steel | No
FLC Puget Sound | 181 | 1134000 | 27000 | Slop | AST | 1977 | 40 | Vertical Cylindrical | 70' x 41' | Steel | No
FLC Puget Sound | 182 | 210000 | 5000 | FOR | AST | 1977 | 40 | Vertical Cylindrical | 30' x 41' | Steel | No
FLC Puget Sound | 19 | 1134000 | 27000 | JP‐5 | UST | 1942 | 75 | Vertical Cylindrical | 100' x 20' | Concrete | No
FLC Puget Sound | 195 | 17010 | 405 | lube Oil | AST | 1987 | 30 | Horizontal Cylindrical | 10' x 30' | Steel | No
FLC Puget Sound | 196 | 17010 | 405 | lube Oil | AST | 1987 | 30 | Horizontal Cylindrical | 10' x 30' | Steel | No
FLC Puget Sound | 197 | 17010 | 405 | lube Oil | AST | 1987 | 30 | Horizontal Cylindrical | 10' x 30' | Steel | No
FLC Puget Sound | 198 | 17010 | 405 | lube Oil | AST | 1987 | 30 | Horizontal Cylindrical | 10' x 30' | Steel | No
FLC Puget Sound | 20 | 1134000 | 27000 | JP‐5 | UST | 1942 | 75 | Vertical Cylindrical | 100' x 20' | Concrete | No
FLC Puget Sound | 21 | 1134000 | 27000 | JP‐5 | UST | 1942 | 75 | Vertical Cylindrical | 100' x 20' | Concrete | No
FLC Puget Sound | 215 | 14994 | 357 | FSII | AST | 1995 | 22 | Vertical Cylindrical | 10'6x24' | Steel | No
FLC Puget Sound | 216 | 14994 | 357 | FSII | AST | 1995 | 22 | Vertical Cylindrical | 10'6x24' | Steel | No
FLC Puget Sound | 22 | 2100000 | 50000 | F‐76 | UST | 1942 | 75 | Vertical Cylindrical | 120' x 25' | Concrete | No
FLC Puget Sound | 23 | 2100000 | 50000 | F‐76 | UST | 1942 | 75 | Vertical Cylindrical | 120' x 25' | Concrete | No
FLC Puget Sound | 24 | 2100000 | 50000 | F‐76 | UST | 1942 | 75 | Vertical Cylindrical | 120' x 25' | Concrete | No |  | Overfill March 1990, approximately 10,000 gallons
FLC Puget Sound | 25 | 2100000 | 50000 | F‐76 | UST | 1942 | 75 | Vertical Cylindrical | 120' x 25' | Concrete | No
FLC Puget Sound | 26 | 2100000 | 50000 | F‐76 | UST | 1942 | 75 | Vertical Cylindrical | 120' x 25' | Concrete | No
FLC Puget Sound | 27 | 2100000 | 50000 | F‐76 | UST | 1942 | 75 | Vertical Cylindrical | 120' x 25' | Concrete | No
FLC Puget Sound | 28 | 2100000 | 50000 | F‐76 | UST | 1942 | 75 | Vertical Cylindrical | 120' x 25' | Concrete | No
FLC Puget Sound | 29 | 2100000 | 50000 | F‐76 | UST | 1942 | 75 | Vertical Cylindrical | 120' x 25' | Concrete | No |  | Overfill February 1990, approximately 38,000 to 40,000 gallons
FLC Puget Sound | 30 | 2100000 | 50000 | F‐76 | UST | 1942 | 75 | Vertical Cylindrical | 120' x 25' | Concrete | No
FLC Puget Sound | 31 | 2100000 | 50000 | JP‐5 | UST | 1942 | 75 | Vertical Cylindrical | 120' x 25' | Concrete | No
FLC Puget Sound | 32 | 2100000 | 50000 | JP‐5 | UST | 1942 | 75 | Vertical Cylindrical | 120' x 25' | Concrete | No
FLC Puget Sound | 33 | 2100000 | 50000 | JP‐5 | UST | 1942 | 75 | Vertical Cylindrical | 120' x 25' | Concrete | No
FLC Puget Sound | 34 | 2100000 | 50000 | JP‐5 | UST | 1942 | 75 | Vertical Cylindrical | 120' x 25' | Concrete | No
FLC Puget Sound | 35 | 2100000 | 50000 | JP‐5 | UST | 1942 | 75 | Vertical Cylindrical | 120' x 25' | Concrete | No
FLC Puget Sound | 36 | 2100000 | 50000 | JP‐5 | UST | 1942 | 75 | Vertical Cylindrical | 120' x 25' | Concrete | No
FLC Puget Sound | 37 | 2100000 | 50000 | JP‐5 | UST | 1942 | 75 | Vertical Cylindrical | 120' x 25' | Concrete | No
FLC Puget Sound | 38 | 1974000 | 47000 | JP‐5 | UST | 1942 | 75 | Vertical Cylindrical | 120' x 25' | Concrete | No
FLC Puget Sound | 39 | 1974000 | 47000 | JP‐5 | UST | 1942 | 75 | Vertical Cylindrical | 120' x 25' | Concrete | No
FLC Puget Sound | 40 | 1974000 | 47000 | JP‐5 | UST | 1942 | 75 | Vertical Cylindrical | 120' x 25' | Concrete | No
FLC Puget Sound | 41 | 1974000 | 47000 | JP‐5 | UST | 1942 | 75 | Vertical Cylindrical | 120' x 25' | Concrete | No
FLC Puget Sound | 42 | 2100000 | 50000 | JP‐5 | UST | 1942 | 75 | Vertical Cylindrical | 120' x 25' | Concrete | No
FLC Puget Sound | 43 | 2100000 | 50000 | JP‐5 | UST | 1942 | 75 | Vertical Cylindrical | 120' x 25' | Concrete | No
FLC Puget Sound | 48 | 1134000 | 27000 | JP‐8 | UST | 1942 | 75 | Vertical Cylindrical | 100' x 20' | Steel | No
FLC Puget Sound | 49 | 1134000 | 27000 | F‐24 | UST | 1942 | 75 | Vertical Cylindrical | 100' x 20' | Steel | No
FLC Puget Sound | 50 | 1134000 | 27000 | F‐24 | UST | 1942 | 75 | Vertical Cylindrical | 100' x 20' | Steel | No
NAS Lemoore | LEM Tank 109 | 25000 | 595 | Jet Fuel | UST | 1996 | 21 |  | 10' x 10' 4 7/8" | DoubleWalled, Fiberglass | No
NAS Lemoore | LEM Tank 764‐A | 10000 | 238 | Diesel | UST | 1989 | 28 |  | 10' x 8' | DoubleWalled, Fiberglass | No
NAS Lemoore | LEM Tank 764‐B | 10000 | 238 | MOGAS | UST | 1989 | 28 |  | 10' x 8' | DoubleWalled, Fiberglass | No
NAS Lemoore | LEM Tank 96 | 25000 | 595 | Diesel | UST | 1996 | 21 |  | 10' x 10' 4 7/8" | DoubleWalled, Fiberglass | No
NAS Lemoore | LEM Tank 98 | 4000 | 95 | Waste | UST | 1996 | 21 |  | 6' x 6'33 1/2" | DoubleWalled, Fiberglass | No
NAS Lemoore | LEM Tank 99 | 25000 | 595 | MOGAS | UST | 1996 | 21 |  | 10' x 10' 4 7/8" | DoubleWalled, Fiberglass | No
NAS Lemoore | LEM Tank J‐1 | 567000 | 13500 | JP‐5 | UST | 1961 | 56 |  | 88' x 13' | Single Wall, Steel in Concrete | No
NAS Lemoore | LEM Tank J‐10 | 105000 | 2500 | JP‐5 | UST | 1961 | 56 |  | 42' x 11' 6" | Single Wall, Steel in Concrete | No
NAS Lemoore | LEM Tank J‐2 | 105000 | 2500 | JP‐5 | UST | 1961 | 56 |  | 42' x 11' 6" | Single Wall, Steel in Concrete | No
NAS Lemoore | LEM Tank J‐20 | 105000 | 2500 | JP‐5 | UST | 1961 | 56 |  | 42' x 11' 6" | Single Wall, Steel in Concrete | No
NAS Lemoore | LEM Tank J‐3 | 567000 | 13500 | JP‐5 | UST | 1961 | 56 |  | 88' x 13' | Single Wall, Steel in Concrete | No
NAS Lemoore | LEM Tank J‐30 | 105000 | 2500 | JP‐5 | UST | 1961 | 56 |  | 42' x 11' 6" | Single Wall, Steel in Concrete | No
NAS Lemoore | LEM Tank J‐4 | 567000 | 13500 | JP‐5 | UST | 1961 | 56 |  | 88' x 13' | Single Wall, Steel in Concrete | No
NAS Lemoore | LEM Tank J‐40 | 105000 | 2500 | JP‐5 | UST | 1961 | 56 |  | 42' x 11' 6" | Single Wall, Steel in Concrete | No
NAS Lemoore | LEM Tank J‐5 | 105000 | 2500 | JP‐5 | UST | 1961 | 56 |  | 42' x 11' 6" | Single Wall, Steel in Concrete | No
NAS Lemoore | LEM Tank J‐50 | 105000 | 2500 | JP‐5 | UST | 1969 | 48 |  | 42' x 11' 6" | Single Wall, Steel in Concrete | No
NAS Lemoore | LEM Tank J‐6 | 567000 | 13500 | JP‐5 | UST | 1961 | 56 |  | 88' x 13' | Single Wall, Steel in Concrete | No
Guantanamo Bay | GBY Tank 1 | 12100 | 288 | Diesel | AST | 1998 | 19 |  | 34'.1.5x8'.05"x8'.9.75" | Convault Tank | No
Guantanamo Bay | GBY Tank 1040‐1 | 5000 | 119 | MOGAS | AST | 1998 | 19 |  | 15'6x8'.05"x8'.9.75"" | Convault Tank | No
Guantanamo Bay | GBY Tank 1040‐2 | 5000 | 119 | MOGAS | AST | 1998 | 19 |  | 15'6x8'.05"x8'.9.75"" | Convault Tank | No
Guantanamo Bay | GBY Tank 1040‐3 | 5000 | 119 | F‐76 | AST | 1998 | 19 |  | 15'6x8'.05"x8'.9.75"" | Convault Tank | No
Guantanamo Bay | GBY Tank 1040‐4 | 5000 | 119 | Diesel | AST | 1998 | 19 |  | 15'6x8'.05"x8'.9.75"" | Convault Tank | No
Guantanamo Bay | GBY Tank 1321‐1 | 5000 | 119 | Diesel | AST | 1989 | 28 |  | 15'6x8'.05"x8'.9.75"" | Convault Tank | No
Guantanamo Bay | GBY Tank 1321‐2 | 5000 | 119 | MOGAS | AST | 1998 | 19 |  | 15'6x8'.05"x8'.9.75"" | Convault Tank | No
Guantanamo Bay | GBY Tank 1321‐3 | 5000 | 119 | MOGAS | AST | 1998 | 19 |  | 15'6x8'.05"x8'.9.75"" | Convault Tank | No
Guantanamo Bay | GBY Tank 2 | 12100 | 288 | Diesel | AST | 1998 | 19 |  | 34'.1.5x8'.05"x8'.9.75" | Convault Tank | No
Guantanamo Bay | GBY Tank 3 | 12100 | 288 | Diesel | AST | 1998 | 19 |  | 34'.1.5x8'.05"x8'.9.75" | Convault Tank | No
Guantanamo Bay | GBY Tank 4 | 12100 | 288 | Diesel | AST | 1998 | 19 |  | 34'.1.5x8'.05"x8'.9.75" | Convault Tank | No
Guantanamo Bay | GBY Tank 5 | 12100 | 288 | Diesel | AST | 1998 | 19 |  | 34'.1.5x8'.05"x8'.9.75" | Convault Tank | No
Guantanamo Bay | GBY Tank 6 | 12100 | 288 | JP‐5 | AST | 1998 | 19 |  | 34'.1.5x8'.05"x8'.9.75" | Convault Tank | No
Guantanamo Bay | GBY Tank 719B | 10000 | 238 | JP‐5 | AST | 1990 | 27 |  | Unknown | Steel | No
Guantanamo Bay | GBY Tank 126 (HV‐1) | 653898 | 15569 | MOGAS | AST | 1913 | 104 |  | 63' Dia | Steel/Encase in concrete | Yes | Small | 23‐Aug‐12 | MOGAS Weeping from loose rivet. | Demo
Guantanamo Bay | GBY Tank 127 (HV‐2) | 642012 | 15286 | MOGAS | AST | 1913 | 104 |  | 63' Dia | Steel/Encase in concrete | No |  |  |  | Sch for Demo
Guantanamo Bay | GBY Tank 527 (LP‐3) | 329658 | 7849 | JP‐5 | UST | 1954 | 63 |  | 55' Dia | Steel | No
Guantanamo Bay | GBY Tank 528 (LP‐4) | 328802 | 7829 | JP‐5 | UST | 1954 | 63 |  | 55' Dia | Steel | No
Guantanamo Bay | GBY Tank 529 | 2304583 | 54871 | JP‐5 | AST | 2013 | 4 |  | Unknown | Steel | No
Guantanamo Bay | GBY Tank 105 | 2227512 | 53036 | F‐76 | UST | 1926 | 91 |  | 139'6x138'10"" | Steel | Yes | Small | 23‐Jan‐02 | Unknown | Tank retrofitted with a new tank built inside of old tank
Guantanamo Bay | GBY Tank 106 | 2215752 | 52756 | F‐76 | UST | 1926 | 91 |  | 139'6x138'10"" | Steel | Yes | Small | 23‐Jan‐02 | Unknown | Tank retrofitted with a new tank built inside of old tank
Guantanamo Bay | GBY Tank 134 (HV‐9) | 1087548 | 25894 | F‐76 | UST | 1942 | 75 |  | 100' Dia | Steel | No
Guantanamo Bay | GBY Tank 154 (HV‐12) | 1056468 | 25154 | JP‐5 | UST | 1942 | 75 |  | 100' Dia | Steel | No
Guantanamo Bay | GBY Tank 156 (HV‐10) | 1087548 | 25894 | JP‐5 | UST | 1942 | 75 |  | 100' Dia | Steel | No
Guantanamo Bay | GBY Tank 602 (LP‐1) | 329658 | 7849 | JP‐5 | UST | 1954 | 63 |  | 55' Dia | Steel | No
Guantanamo Bay | GBY Tank 603 (LP‐2) | 327222 | 7791 | JP‐5 | UST | 1954 | 63 |  | 55' Dia | Steel | No
[6 empty] | Total Tank Yrs | 10725 |  |  |  | Small Release (<1000g) | 12
[6 empty] | Total Tank Hrs | 94015350 |  |  |  | Large Release (>1000g) | 0
|  |  |  | UST | 121 | UST Years | 7050 | Small | 10
|  |  |  | AST | 80 | AST Years | 3675 | Large | 0
[8 empty] | Small Lambda / hour | 1.6183e-07
[8 empty] | Large Lambda / hour | 0
[8 empty] | Small Lambda / Year | 0.0014184
[8 empty] | Large Lambda / Year | 0
| Releases | Tank Years
Sasebo‐Akasaki | 0 | 100
Sasebo‐Iorizaki | 0 | 128
Sasebo‐Yokose | 1 | 229
Hakozaki | 6 | 998
NB Guam | 1 | 1658
FLC Puget Sound | 0 | 2530
NAS Lemoore | 0 | 748
Guantanamo Bay | 2 | 659
the numerical value "1,97" seems to have a typo in it.
Due to the comma which is meant as a 3 digit seperator we don't know if this is "197" or "1,970".
If the comma as not there, it would be 197, with the comma there is a reason to believe that it may have been 1,970 but the "0" was left out.
The rows with the "Release?" column left blank are assumbed to be no incident.
In other words the tanks operated since the construction year without any releases.
Currently the row with "Release?" data of "Maybe" is assumed as no release. In the next update we will consider this to be a release incident to be on the conservative side.

## OGP
OGP Report No. 434 – 3 March 2010
2.0 Summary of Recommended Data
Tank Description | Failure Mode | Leak Frequency (per tank year) | Leak Frequency (per hour)
Atmospheric Storage Tanks Fixed/ floating roof | Liquid spill outside tank | 0.0028 | 3.1945e-07
| Tank rupture | 3e-06 | 3.4227e-10
4.0 Review of Data Sources
Failure experience was reviewed from a number of sources:
• [3] includes 122 cases of atmospheric storage tank fires world-wide during 1965-89.
• [4] lists 69 such events during 1981-96.
• [5] lists 107 events during 1951-95 (see [1] App I).

## Verified Reports
Unverified Histories: Releases Vs Tell-tales AND Verified Reporting: Since 1988
**Note that the unverified histories seldom distinguish between leak tests conducted with fuel and water or controlled releases during leak tests vs UFMs, sample lines, and/or tell-tales. Additional research through verified source documents is/and continues to occur to provide additional/proper context of releases in order to support current/future QRVA/RVAs.
LeakTesting |  |  | Water |  |  | Water/Fuel |  |  | ND | JP5 | JP8 | DO |  | Not Specified
Tank 01 | Year ('XX) | 70 | 71 | 71 | 72 | 75 | 82 | 82 | 83 | 83 | 83 |  |  | Release | Tell-tale
| Period (days) | 63 | 191 | 37 | 56 | 6 | 6 | 55 | 76 | 23 | 38
| Release (gals) | 4623 | 16830 | 5031 | 4810 | 10671 | 2417 | 871 | 2229 | -1090 | -1004 |  |  | 45388
| Year ('XX) | 47 | 53 | 64 | 64 | 64 | 65 | 65 | 66 | 67 | 77 | 78 | 78
| Period (days) | 0.0055556 |  | 0.0027778 | 0.041667 | [5 empty] | 75 | 114 | 127
| Tell-tale (gals) | 5 | u/k | 0.25 | 0.25 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 999 | 7874 | 13221 |  | 22099.55
Tank 02 | Year ('XX)
Period (days)
Release (gals)
| Year ('XX) | 47 | 54 | 54
| Period (days) |  | 0.083333 | 0.29167
| Tell-tale (gals) | u/k | 0.375 | 10
Tank 03 | Year ('XX) | 49
| Period (days) | 71
| Release (gals) | 4260 | [11 empty] | 4260
Year ('XX)
Period (days)
Tell-tale (gals)
Tank 04 | Year ('XX)
Period (days)
Release (gals)
Year ('XX)
Period (days)
Tell-tale (gals)
Tank 05 | Year ('XX) | 14
Period (days)
| Release (gals) | 27000 | [11 empty] | 27000
| Year ('XX) | 64 | 72
| Period (days) | 0.041667 | 1
| Tell-tale (gals) | 1 | 0.5 | [11 empty] | 1.5
Tank 06 | Year ('XX)
Period (days)
Release (gals)
Year ('XX)
Period (days)
Tell-tale (gals)
Tank 07 | Year ('XX) | 81
Period (days)
| Release (gals) | 6505 | [11 empty] | 6505
| Year ('XX) | 78
Period (days)
| Tell-tale (gals) | u/k | [12 empty] | 0
Tank 08 | Year ('XX)
Period (days)
Release (gals)
Year ('XX)
Period (days)
Tell-tale (gals)
Tank 09 | Year ('XX) | 80
| Period (days) | 258
| Release (gals) | 1900 | [11 empty] | 1900
| Year ('XX) | 58
Period (days)
| Tell-tale (gals) | 1500 | [12 empty] | 1500
Tank 10 | Year ('XX) | 80
| Period (days) | 307
| Release (gals) | 3123.1 | [11 empty] | 3123.1 |  | Not mentioned in GPP
| Year ('XX) | 73
| Period (days) | 3
| Tell-tale (gals) | 0.01 | [12 empty] | 0.01
Tank 11 | Year ('XX) | 80
| Period (days) | 34
| Release (gals) | 25628 | [11 empty] | 25628 |  | Higher than GPP of 20,000
Year ('XX)
Period (days)
Tell-tale (gals)
Tank 12 | Year ('XX) | 81
| Period (days) | 2
| Release (gals) | 4280 | [11 empty] | 4280 |  | Undefined in GPP
Year ('XX)
Period (days)
Tell-tale (gals)
Tank 13 | Year ('XX)
Period (days)
Release (gals)
Year ('XX)
Period (days)
Tell-tale (gals)
Tank 14 | Year ('XX)
Period (days)
Release (gals)
Year ('XX)
Period (days)
Tell-tale (gals)
Tank 15 | Year ('XX) | 81
Period (days)
| Release (gals) | u/k | [11 empty] | 0
Year ('XX)
Period (days)
Tell-tale (gals)
Tank 16 | Year ('XX) | 48 | 98 | [12 empty] | 98 release confirmed incorrect
| Period (days) |  | 31 | [12 empty] | per referenced source doc. No
| Release (gals) | u/k | 1469 | [10 empty] | 0 |  | leaks documented in that report.
| Year ('XX) | 49 | 49 | 73 | 81
| Period (days) | 11 | 4
| Tell-tale (gals) | 11009 | 17737 | 0.01 | u/k | [9 empty] | 28746.01
Tank 17 | Year ('XX) | 49
| Period (days) | 71
| Release (gals) | 1420 | [11 empty] | 1420
| Year ('XX) | 69 | 75
| Period (days) | 0.0010417
| Tell-tale (gals) | 1 | u/k | [11 empty] | 1
Tank 18 | Year ('XX)
Period (days)
Release (gals)
Year ('XX)
Period (days)
Tell-tale (gals)
Tank 19 | Year ('XX)
Period (days)
Release (gals)
| Year ('XX) | 64
| Period (days) | 40
| Tell-tale (gals) | 0.66
Tank 20 | Year ('XX)
Period (days)
Release (gals)
Year ('XX)
Period (days)
Tell-tale (gals)
[14 empty] | 119504.1 | 52348.07

## NUREG_OGP_Navy_RH
| Leak Type | λ / yr | λ / hr
NUREC CR 6928
| Small (< 50 gpm) | 0.00028048 | 3.2e-08
| Large (> 50 gpm) | 1.9809e-05 | 2.26e-09
OGP (Atmospheric Storage Tanks, Fixed/ floating roof)
Floating roof | Liquid spill on roof | 0.0016 | 1.8254e-07
| Sunken roof | 0.0011 | 1.255e-07
Fixed/ floating roof | Liquid spill outside tank | 0.0028 | 3.1945e-07
| Tank rupture | 3e-06 | 3.4227e-10
NavyBulkTank_SpillReleaseData (UST)
| Small (<1000 g) | 0.00099291 | 1.1328e-07
| Large (> 1000 g) | 0.00028369 | 3.2366e-08
Red Hill (Small < 2gpm)
| wo Telltale | 0.014336 | 1.6355e-06
| w Telltale | 0.035907 | 4.0966e-06