## SummaryAllTanks
Generic Distribution from NUREG CR 6928 (Industry average for 47,023,680 tank hours)
Tank (Unpressurized) |  |  | Failure Mode | Distribution Type | Mean (failures / hour) | Alpha | Beta | Error Factor
External Leak Small (1 to 50 gpm.) |  |  | TNK UNPR ELS | Gamma | 3.19e-08 | 0.5 | 15670000 | 8.4
External Leak Large (> 50 gpm. Small leak times 0.07.) |  |  | TNK UNPR ELL | Gamma | 2.23e-09 | 0.3 | 134400000 | 18.8
Generic Distribution from NUREG CR 6928 In RISKMAN (Prior)
RM DIST. | Failure Mode | Distribution Type |  | Mean (failures / hour) | 5th | Median | 95th | Error Factor
TNKELS | External Leak Small | Gamma |  | 3.2e-08 | 1.06e-10 | 1.32e-08 | 1.137e-07 | 8.6136
TNKELL | External Leak Large | Gamma |  | 2.26e-09 | 1.82e-13 | 4.74e-10 | 9.28e-09 | 19.5781
First Stage Update Using NavyBulkTank_SpillReleaseData In RISKMAN (Average for 876,600 tank hours) (Posterior)
RM DIST. | Failure Mode | Distribution Type | No. Releases | Mean (failures / hour) | 5th | Median | 95th | Error Factor
TKELSU | External Leak Small | One-Stage Update | 9 | 5.73e-07 | 3e-07 | 5.44e-07 | 8.87e-07 | 1.6305
TKELLU | External Leak Large | One-Stage Update | 2 | 1.71e-08 | 3.43e-09 | 1.41e-08 | 3.71e-08 | 2.6312
Second Stage Update Using RedHill Specific Data for Tank 1 - 20 (over 350,640 hours) (Posterior) Using NavyBulkTank_SpillReleaseData | [8 empty] | First Stage Update Using RedHill Specific Data for Tank 1 - 20 (over 350,640 hours) (Posterior) W.O. Using NavyBulkTank_SpillReleaseData
RM DIST. | Failure Mode | Distribution Type | No. Releases | Mean (failures / hour) | 5th | Median | 95th | Error Factor | RM DIST. | Failure Mode | Distribution Type | No. Releases | Mean (failures / hour) | 5th | Median | 95th | Error Factor
TNK1S | Tank 1 External Leak Small | Two-Stage Update | 4 | 8.09e-07 | 4.69e-07 | 7.61e-07 | 1.19e-06 | 1.5637 | TK1S | Tank 1 External Leak Small | One-Stage Update | 4 | 2.81e-07 | 1.01e-07 | 2.54e-07 | 5.1e-07 | 2.0079
TNK1L | Tank 1 External Leak Large | Two-Stage Update | 3 | 4.2e-08 | 1.56e-08 | 3.6e-08 | 7.25e-08 | 2.0139 | TK1L | Tank 1 External Leak Large | One-Stage Update | 3 | 2.46e-08 | 7.03e-09 | 2.15e-08 | 4.83e-08 | 2.2465
TK2SU | Tank 2 External Leak Small | Two-Stage Update | 2 | 6.81e-07 | 3.74e-07 | 6.48e-07 | 1.03e-06 | 1.5895 | TK2S | Tank 2 External Leak Small | One-Stage Update | 2 | 1.56e-07 | 3.43e-08 | 1.31e-07 | 3.31e-07 | 2.5267
TK2LU | Tank 2 External Leak Large | Two-Stage Update | 0 | 1.71e-08 | 3.41e-09 | 1.41e-08 | 3.69e-08 | 2.617 | TK2L | Tank 2 External Leak Large | One-Stage Update | 0 | 2.25e-09 | 1.84e-13 | 4.74e-10 | 9.27e-09 | 19.557
TK3SU | Tank 3 External Leak Small | Two-Stage Update | 0 | 5.61e-07 | 2.93e-07 | 5.33e-07 | 8.71e-07 | 1.6341 | TK3S | Tank 3 External Leak Small | One-Stage Update | 0 | 3.09e-08 | 1.03e-10 | 1.27e-08 | 1.09e-07 | 8.5827
TK3LU | Tank 3 External Leak Large | Two-Stage Update | 0 | 1.71e-08 | 3.41e-09 | 1.41e-08 | 3.69e-08 | 2.617 | TK3L | Tank 3 External Leak Large | One-Stage Update | 0 | 2.25e-09 | 1.84e-13 | 4.74e-10 | 9.27e-09 | 19.557
TK4SU | Tank 4 External Leak Small | Two-Stage Update | 0 | 5.61e-07 | 2.93e-07 | 5.33e-07 | 8.71e-07 | 1.6341 | TK4S | Tank 4 External Leak Small | One-Stage Update | 0 | 3.09e-08 | 1.03e-10 | 1.27e-08 | 1.09e-07 | 8.5827
TK4LU | Tank 4 External Leak Large | Two-Stage Update | 0 | 1.71e-08 | 3.41e-09 | 1.41e-08 | 3.69e-08 | 2.617 | TK4L | Tank 4 External Leak Large | One-Stage Update | 0 | 2.25e-09 | 1.83e-13 | 4.73e-10 | 9.25e-09 | 19.556
TK5SU | Tank 5 External Leak Small | Two-Stage Update | 2 | 6.81e-07 | 3.74e-07 | 6.48e-07 | 1.03e-06 | 1.5895 | TK5S | Tank 5 External Leak Small | One-Stage Update | 2 | 1.56e-07 | 3.43e-08 | 1.31e-07 | 3.31e-07 | 2.5267
TK5LU | Tank 5 External Leak Large | Two-Stage Update | 1 | 2.46e-08 | 6.72e-09 | 2.12e-08 | 4.89e-08 | 2.3066 | TK5L | Tank 5 External Leak Large | One-Stage Update | 1 | 9.7e-09 | 8.23e-10 | 6.99e-09 | 2.51e-08 | 3.5908
TK6SU | Tank 6 External Leak Small | Two-Stage Update | 1 | 6.21e-07 | 3.34e-07 | 5.91e-07 | 9.52e-07 | 1.6108 | TK6S | Tank 6 External Leak Small | One-Stage Update | 1 | 9.36e-08 | 1.03e-08 | 7.05e-08 | 2.31e-07 | 3.2766
TK6LU | Tank 6 External Leak Large | Two-Stage Update | 0 | 1.71e-08 | 3.41e-09 | 1.41e-08 | 3.69e-08 | 2.617 | TK6L | Tank 6 External Leak Large | One-Stage Update | 0 | 2.25e-09 | 1.83e-13 | 4.73e-10 | 9.25e-09 | 19.556
TK7SU | Tank 7 External Leak Small | Two-Stage Update | 2 | 6.81e-07 | 3.74e-07 | 6.48e-07 | 1.03e-06 | 1.5895 | TK7S | Tank 7 External Leak Small | One-Stage Update | 2 | 1.56e-07 | 3.43e-08 | 1.31e-07 | 3.31e-07 | 2.5267
TK7LU | Tank 7 External Leak Large | Two-Stage Update | 1 | 2.46e-08 | 6.72e-09 | 2.12e-08 | 4.89e-08 | 2.3066 | TK7L | Tank 7 External Leak Large | One-Stage Update | 1 | 9.7e-09 | 8.23e-10 | 6.99e-09 | 2.51e-08 | 3.5908
TK8SU | Tank 8 External Leak Small | Two-Stage Update | 0 | 5.61e-07 | 2.93e-07 | 5.33e-07 | 8.71e-07 | 1.6341 | TK8S | Tank 8 External Leak Small | One-Stage Update | 0 | 3.09e-08 | 1.03e-10 | 1.27e-08 | 1.09e-07 | 8.5827
TK8LU | Tank 8 External Leak Large | Two-Stage Update | 0 | 1.71e-08 | 3.41e-09 | 1.41e-08 | 3.69e-08 | 2.617 | TK8L | Tank 8 External Leak Large | One-Stage Update | 0 | 2.25e-09 | 1.84e-13 | 4.74e-10 | 9.27e-09 | 19.557
TK9SU | Tank 9 External Leak Small | Two-Stage Update | 2 | 6.81e-07 | 3.74e-07 | 6.48e-07 | 1.03e-06 | 1.5895 | TK9S | Tank 9 External Leak Small | One-Stage Update | 2 | 1.56e-07 | 3.43e-08 | 1.31e-07 | 3.31e-07 | 2.5267
TK9LU | Tank 9 External Leak Large | Two-Stage Update | 0 | 1.71e-08 | 3.41e-09 | 1.41e-08 | 3.69e-08 | 2.617 | TK9L | Tank 9 External Leak Large | One-Stage Update | 0 | 2.25e-09 | 1.84e-13 | 4.74e-10 | 9.27e-09 | 19.557
TK10SU | Tank 10 External Leak Small | Two-Stage Update | 3 | 7.43e-07 | 4.21e-07 | 7.05e-07 | 1.11e-06 | 1.5745 | TK10S | Tank 10 External Leak Small | One-Stage Update | 3 | 2.18 | 6.54e-08 | 1.92e-07 | 4.22e-07 | 2.1979
TK10LU | Tank 10 External Leak Large | Two-Stage Update | 0 | 1.71e-08 | 3.41e-09 | 1.41e-08 | 3.69e-08 | 2.617 | TK10L | Tank 10 External Leak Large | One-Stage Update | 0 | 2.25e-09 | 1.84e-13 | 4.74e-10 | 9.27e-09 | 19.557
TK11SU | Tank 11 External Leak Small | Two-Stage Update | 0 | 5.61e-07 | 2.93e-07 | 5.33e-07 | 8.71e-07 | 1.6341 | TK11S | Tank 11 External Leak Small | One-Stage Update | 0 | 3.09e-08 | 1.03e-10 | 1.27e-08 | 1.09e-07 | 8.5827
TK11LU | Tank 11 External Leak Large | Two-Stage Update | 1 | 2.46e-08 | 6.72e-09 | 2.12e-08 | 4.89e-08 | 2.3066 | TK11L | Tank 11 External Leak Large | One-Stage Update | 1 | 9.7e-09 | 8.23e-10 | 6.99e-09 | 2.51e-08 | 3.5908
TK12SU | Tank 12 External Leak Small | Two-Stage Update | 2 | 6.81e-07 | 3.74e-07 | 6.48e-07 | 1.03e-06 | 1.5895 | TK12S | Tank 5 External Leak Small | One-Stage Update | 2 | 1.56e-07 | 3.43e-08 | 1.31e-07 | 3.31e-07 | 2.5267
TK12LU | Tank 12 External Leak Large | Two-Stage Update | 1 | 2.46e-08 | 6.72e-09 | 2.12e-08 | 4.89e-08 | 2.3066 | TK12L | Tank 5 External Leak Large | One-Stage Update | 1 | 9.7e-09 | 8.23e-10 | 6.99e-09 | 2.51e-08 | 3.5908
TK13SU | Tank 13 External Leak Small | Two-Stage Update | 1 | 6.21e-07 | 3.34e-07 | 5.91e-07 | 9.52e-07 | 1.6108 | TK13S | Tank 13 External Leak Small | One-Stage Update | 1 | 9.36e-08 | 1.03e-08 | 7.05e-08 | 2.31e-07 | 3.2766
TK13LU | Tank 13 External Leak Large | Two-Stage Update | 0 | 1.71e-08 | 3.41e-09 | 1.41e-08 | 3.69e-08 | 2.617 | TK13L | Tank 13 External Leak Large | One-Stage Update | 0 | 2.25e-09 | 1.83e-13 | 4.73e-10 | 9.25e-09 | 19.556
TK14SU | Tank 14 External Leak Small | Two-Stage Update | 0 | 5.61e-07 | 2.93e-07 | 5.33e-07 | 8.71e-07 | 1.6341 | TK14S | Tank 14 External Leak Small | One-Stage Update | 0 | 3.09e-08 | 1.03e-10 | 1.27e-08 | 1.09e-07 | 8.5827
TK14LU | Tank 14 External Leak Large | Two-Stage Update | 0 | 1.71e-08 | 3.41e-09 | 1.41e-08 | 3.69e-08 | 2.617 | TK14L | Tank 14 External Leak Large | One-Stage Update | 0 | 2.25e-09 | 1.84e-13 | 4.74e-10 | 9.27e-09 | 19.557
TK15SU | Tank 15 External Leak Small | Two-Stage Update | 1 | 6.21e-07 | 3.34e-07 | 5.91e-07 | 9.52e-07 | 1.6108 | TK15S | Tank 15 External Leak Small | One-Stage Update | 1 | 9.36e-08 | 1.03e-08 | 7.05e-08 | 2.31e-07 | 3.2766
TK15LU | Tank 15 External Leak Large | Two-Stage Update | 0 | 1.71e-08 | 3.41e-09 | 1.41e-08 | 3.69e-08 | 2.617 | TK15L | Tank 15 External Leak Large | One-Stage Update | 0 | 2.25e-09 | 1.83e-13 | 4.73e-10 | 9.25e-09 | 19.556
TK16SU | Tank 16 External Leak Small | Two-Stage Update | 3 | 7.43e-07 | 4.21e-07 | 7.05e-07 | 1.11e-06 | 1.5745 | TK16S | Tank 16 External Leak Small | One-Stage Update | 3 | 2.18 | 6.54e-08 | 1.92e-07 | 4.22e-07 | 2.1979
TK16LU | Tank 16 External Leak Large | Two-Stage Update | 3 | 4.2e-08 | 1.56e-08 | 3.6e-08 | 7.25e-08 | 2.0139 | TK16L | Tank 16 External Leak Large | One-Stage Update | 3 | 2.46e-08 | 7.03e-09 | 2.15e-08 | 4.83e-08 | 2.2465
TK17SU | Tank 17 External Leak Small | Two-Stage Update | 2 | 6.81e-07 | 3.74e-07 | 6.48e-07 | 1.03e-06 | 1.5895 | TK17S | Tank 17 External Leak Small | One-Stage Update | 2 | 1.56e-07 | 3.43e-08 | 1.31e-07 | 3.31e-07 | 2.5267
TK17LU | Tank 17 External Leak Large | Two-Stage Update | 0 | 1.71e-08 | 3.41e-09 | 1.41e-08 | 3.69e-08 | 2.617 | TK17L | Tank 17 External Leak Large | One-Stage Update | 0 | 2.25e-09 | 1.84e-13 | 4.74e-10 | 9.27e-09 | 19.557
TK18SU | Tank 18 External Leak Small | Two-Stage Update | 0 | 5.61e-07 | 2.93e-07 | 5.33e-07 | 8.71e-07 | 1.6341 | TK18S | Tank 18 External Leak Small | One-Stage Update | 0 | 3.09e-08 | 1.03e-10 | 1.27e-08 | 1.09e-07 | 8.5827
TK18LU | Tank 18 External Leak Large | Two-Stage Update | 0 | 1.71e-08 | 3.41e-09 | 1.41e-08 | 3.69e-08 | 2.617 | TK18L | Tank 18 External Leak Large | One-Stage Update | 0 | 2.25e-09 | 1.84e-13 | 4.74e-10 | 9.27e-09 | 19.557
TK19SU | Tank 19 External Leak Small | Two-Stage Update | 2 | 6.81e-07 | 3.74e-07 | 6.48e-07 | 1.03e-06 | 1.5895 | TK19S | Tank 19 External Leak Small | One-Stage Update | 2 | 1.56e-07 | 3.43e-08 | 1.31e-07 | 3.31e-07 | 2.5267
TK19LU | Tank 19 External Leak Large | Two-Stage Update | 0 | 1.71e-08 | 3.41e-09 | 1.41e-08 | 3.69e-08 | 2.617 | TK19L | Tank 19 External Leak Large | One-Stage Update | 0 | 2.25e-09 | 1.84e-13 | 4.74e-10 | 9.27e-09 | 19.557
TK20SU | Tank 20 External Leak Small | Two-Stage Update | 0 | 5.61e-07 | 2.93e-07 | 5.33e-07 | 8.71e-07 | 1.6341 | TK20S | Tank 20 External Leak Small | One-Stage Update | 0 | 3.09e-08 | 1.03e-10 | 1.27e-08 | 1.09e-07 | 8.5827
TK20LU | Tank 20 External Leak Large | Two-Stage Update | 0 | 1.71e-08 | 3.41e-09 | 1.41e-08 | 3.69e-08 | 2.617 | TK20L | Tank 20 External Leak Large | One-Stage Update | 0 | 2.25e-09 | 1.84e-13 | 4.74e-10 | 9.27e-09 | 19.557

## Tank Overfill Estimate
10 | facility fill operations per year
30 | facility internal transfer operations per year
18 | active tanks in facility
2.2222 | fill operations per tank per year
0.000815 | high level switch fails to actuate/demand
0.0018111 | per tank per year
0.0326 | per facility per year

## RedHill Release Incidents
| Date | Tank | Quantity (gallons) | Rate | Type | Detection Method | Mitigation | Cause | Data Source
| 1947 | 1 |  | 0.625 gallons / minute | JP-5 | Telltale |  |  | EPA-R09-UST-2015-0441-0559 (1).pdf RH_Tank01_UnverifiedHistory.PDF RH_Tank02_UnverifiedHistory.PDF
| 1947 Oct. | 2 |  |  | JP-5 | telltale | tank emptied |  | RH_Tank02_UnverifiedHistory.PDF EPA-R09-UST-2015-0441-0559 (1).pdf
| 1948 Jul. | 16 | 11000 |  |  | telltale | tank emptied |  | RH_Tank16_UnverifiedHistory.PDF EPA-R09-UST-2015-0441-0559 (1).pdf
| 1949 Dec. | 16 | 18000 |  |  | telltale |  |  | RH_Tank16_UnverifiedHistory.PDF EPA-R09-UST-2015-0441-0559 (1).pdf
| 1953 Aug. | 1 |  |  | JP-5 | crack found in tank |  | crack found in tank | RH_Tank01_UnverifiedHistory.PDF EPA-R09-UST-2015-0441-0559 (1).pdf
| 1954 May | 2 |  | 10 gallons in 7 hours | JP-5 |  |  |  | EPA-R09-UST-2015-0441-0559 (1).pdf RH_Tank02_UnverifiedHistory.PDF
| 1958 Apr. | 9 | 1500 |  | DFM | telltale |  |  | RH_Tank09_UnverifiedHistory.PDF EPA-R09-UST-2015-0441-0559 (1).pdf
| 1964 Jan. | 12 |  |  | DFM |  |  | dome section leak identified | RH_Tank12_UnverifiedHistory.PDF EPA-R09-UST-2015-0441-0559 (1).pdf
| 1964 Jun. | 19 |  | 5 mL/hr. | JP-5 | telltale |  | weld leak discovered, | RH_Tank19_UnverifiedHistory.PDF EPA-R09-UST-2015-0441-0559 (1).pdf
| 1964 Aug. | 1 |  | 1 quart per 2.5 minutes | JP-5 |  |  |  | RH_Tank01_UnverifiedHistory.PDF EPA-R09-UST-2015-0441-0559 (1).pdf
| 1965 Mar. | 5 |  | 1 gallon per 1.25 hours | JP-5 |  |  |  | RH_Tank05_UnverifiedHistory.PDF EPA-R09-UST-2015-0441-0559 (1).pdf
| 1969 Jun. | 17 |  | gallon per 1.5 minutes | JP-5 | telltale |  |  | RH_Tank17_UnverifiedHistory.PDF EPA-R09-UST-2015-0441-0559 (1).pdf
| 1970 Aug. | 1 | 31294 | over(Aug. 1970 and Apr. 1972) | JP-5 | unexplained fuel drops |  |  | RH_Tank01_UnverifiedHistory.PDF EPA-R09-UST-2015-0441-0559 (1).pdf
| 1972 Feb. | 5 |  | 2 quarts per day | JP-5 | telltale |  |  | RH_Tank05_UnverifiedHistory.PDF EPA-R09-UST-2015-0441-0559 (1).pdf
| 1973 Jan. | 10 |  |  | DFM | leak suspected | tank emptied |  | RH_Tank10_UnverifiedHistory.PDF EPA-R09-UST-2015-0441-0559 (1).pdf
| 1973 May | 16 |  | 1 drop per 20 seconds |  | telltale |  |  | RH_Tank16_UnverifiedHistory.PDF EPA-R09-UST-2015-0441-0559 (1).pdf
| 1973 Mar. | 12 |  |  | DFM | suspected leak | tank emptied |  | RH_Tank12_UnverifiedHistory.PDF EPA-R09-UST-2015-0441-0559 (1).pdf
| 1973 Nov. | 7 |  |  | DFM | telltale | tank emptied |  | RH_Tank07_UnverifiedHistory.PDF EPA-R09-UST-2015-0441-0559 (1).pdf
| 1975 Jan. | 17 |  |  | JP-5 | telltale |  |  | RH_Tank17_UnverifiedHistory.PDF EPA-R09-UST-2015-0441-0559 (1).pdf
| 1975 May | 1 | 32765 | over(May 1975 and Aug. 1978) | JP-5 | unexplained fuel drops |  |  | RH_Tank01_UnverifiedHistory.PDF EPA-R09-UST-2015-0441-0559 (1).pdf
| 1976 Apr. | 10 |  |  | DFM | telltale | tank emptied |  | RH_Tank10_UnverifiedHistory.PDF EPA-R09-UST-2015-0441-0559 (1).pdf
| 1976 May | 13 |  |  | DFM | reported as leaking |  |  | RH_Tank13_UnverifiedHistory.PDF EPA-R09-UST-2015-0441-0559 (1).pdf
| 1978 May | 7 |  | significant telltale leak | DFM | telltale | tank emptied |  | RH_Tank07_UnverifiedHistory.PDF EPA-R09-UST-2015-0441-0559 (1).pdf
| 1978 Jul. | 9 |  | 4.5 to 17.9 gallons/day | DFM | Leak test | no documentation of any actions taken to mitigate | after the repair project | RH_Tank09_UnverifiedHistory.PDF EPA-R09-UST-2015-0441-0559 (1).pdf
| 1980 Feb. | 7 | 6505 | rate dropped to< 13 gallons per day below 207 foot fill level | DFM |  |  |  | RH_Tank07_UnverifiedHistory.PDF EPA-R09-UST-2015-0441-0559 (1).pdf
| 1980 Aug. | 11 | 15000 | 10,000 to 20,000 gallons 1,000 to 1,500 gallons per day | DFM |  | emptied and repaired |  | RH_Tank11_UnverifiedHistory.PDF EPA-R09-UST-2015-0441-0559 (1).pdf
| 1981 | 16 |  | leaking badly |  |  |  | after repairs when filled to 242-foot level | RH_Tank16_UnverifiedHistory.PDF EPA-R09-UST-2015-0441-0559 (1).pdf
| 1981 Jan. | 10 |  | severe leak near the top of the tank (between the 235- and 242-foot level) | DFM |  | tank emptied |  | RH_Tank10_UnverifiedHistory.PDF EPA-R09-UST-2015-0441-0559 (1).pdf
| 1981 Feb. | 12 |  | 1,440 gallons per day at the 100-foot level | DFM |  |  | after repairs | RH_Tank12_UnverifiedHistory.PDF EPA-R09-UST-2015-0441-0559 (1).pdf
| 1981 Jul. | 15 |  | leaking badly | DFM |  |  | after tank repair and lining | RH_Tank15_UnverifiedHistory.PDF EPA-R09-UST-2015-0441-0559 (1).pdf
| 1981 Oct. | 16 |  | leaking badly |  |  |  | after repairs and lining | RH_Tank16_UnverifiedHistory.PDF EPA-R09-UST-2015-0441-0559 (1).pdf
| 1982 July | 1 | 5517 | over (Jul. 1982 to Jan. 1983) | JP-5 | drops in fuel level |  |  | RH_Tank01_UnverifiedHistory.PDF EPA-R09-UST-2015-0441-0559 (1).pdf
| 1998 | 19 |  |  | JP-5 | back seepage |  |  | EPA-R09-UST-2015-0441-0559 (1).pdf
| 1998 Oct. | 16 | 1469 | 71 gal/day (over 30.7 days) |  | Tank level drop; petroleum found under base of tank | tank emptied |  | EPA-R09-UST-2015-0441-0559 (1).pdf
| 1999 Sep. | 1 |  | steady stream | JP-5 | Leak into Lower Access Tunnel |  |  | EPA-R09-UST-2015-0441-0559 (1).pdf
| 2002 Apr. | 6 |  |  | JP-5 | taken out of service after a confirmed release |  |  | EPA-R09-UST-2015-0441-0559 (1).pdf
| 2014 Jan. 13 | 5 | 27000 |  | JP-5 | fuel loss | Fuel transferred to other tanks | After inspection (tests) | EPA-R09-UST-2015-0441-0559 (1).pdf red-hill-aoc-press-release (1).pdf
| Years | Incidents | Total release (Gallons)
Total: | 65 | 37 | 150050
Per Year: |  | 0.56923 | 2308.4615
# incidents with sizeable leaks for 20 tanks. |  |  | 10
3.2468e-06
| Tank 1 | 7
| tank 2 | 2
| Tank 3 | 0
| Tank 4 | 0
| Tank 5 | 3
| Tank 6 | 1
| Tank 7 | 3
| Tank 8 | 0
| Tank 9 | 2
| Tank 10 | 3
| Tank 11 | 1
| Tank 12 | 3
| Tank 13 | 1
| Tank 14 | 0
| Tank 15 | 1
| Tank 16 | 6
| Tank 17 | 2
| Tank 18 | 0
| Tank 19 | 2
| Tank 20 | 0

## Sheet2
Inc. Count
1947 | 2
1948 | 1
1949 | 1
1950
1951
1952
1953 | 1
1954 | 1
1955
1956
1957
1958 | 1
1959
1960
1961
1962
1963
1964 | 3
1965 | 1
1966
1967
1968
1969 | 1
1970 | 1
1971
1972 | 1
1973 | 4
1974
1975 | 2
1976 | 2
1977
1978 | 2
1979
1980 | 2
1981 | 5
1982 | 1
1983
1984
1985
1986
1987
1988
1989
1990
1991
1992
1993
1994
1995
1996
1997
1998 | 2
1999 | 1
2000
2001
2002 | 1
2003
2004
2005
2006
2007
2008
2009
2010
2011
2012
2013
2014 | 1
37

## NavyBulkTank_SpillReleaseData
Earliest Date | 1913
Final Date | 2013
Total Years | 100
Small Releases | 9
Large Releases | 2
11

## Tank 1
| Date | Tank | Quantity (gallons) | Small / Large | Rate | Type | Detection Method | Mitigation | Cause | Data Source | Comments
| 1947 | 1 |  | Small | 0.625 gallons / minute | JP-5 | Telltale |  |  | EPA-R09-UST-2015-0441-0559 (1).pdf RH_Tank01_UnverifiedHistory.PDF RH_Tank02_UnverifiedHistory.PDF
| 1953 Aug. | 1 |  | Small |  | JP-5 | crack found in tank |  | crack found in tank | EPA-R09-UST-2015-0441-0559 (1).pdf
| 1964 Aug. | 1 |  | Small | 1 quart per 2.5 minutes | JP-5 |  |  |  | EPA-R09-UST-2015-0441-0559 (1).pdf
| 1970 Aug. | 1 | 31294 | Large | over(Aug. 1970 and Apr. 1972) | JP-5 | unexplained fuel drops |  |  | EPA-R09-UST-2015-0441-0559 (1).pdf
| 1975 May | 1 | 32765 | Large | over(May 1975 and Aug. 1978) | JP-5 | unexplained fuel drops |  |  | EPA-R09-UST-2015-0441-0559 (1).pdf
| 1982 July | 1 | 5517 | Large | over (Jul. 1982 to Jan. 1983) | JP-5 | drops in fuel level |  |  | EPA-R09-UST-2015-0441-0559 (1).pdf
| 1999 Sep. | 1 |  | Small | steady stream | JP-5 | Leak into Lower Access Tunnel |  |  | EPA-R09-UST-2015-0441-0559 (1).pdf
| Years | Incidents | Total release (Gallons)
Total: | 65 | 7 | 69576
Per Year: |  | 0.10769 | 1070.4
# incidents with sizeable leaks for 20 tanks. |  |  | 3
|  |  | Small Leaks | 4
|  |  | Large Leaks | 3
| Second Stage Update Using RedHill Specific Data for Tank 1 | [9 empty] | First Stage Update Using RedHill Specific Data for Tank 1 (wo the NavyBulkTank_SpillReleaseData update)
| RM DIST. | Failure Mode | Distribution Type | No. Releases | Mean | 5th | Median | 95th | Error Factor |  | RM DIST. | Failure Mode | Distribution Type | No. Releases | Mean | 5th | Median | 95th | Error Factor
| TNK1S | Tank 1 External Leak Small | Two-Stage Update | 4 | 8.09e-07 | 4.69e-07 | 7.61e-07 | 1.19e-06 | 1.5637 |  | TK1S | Tank 1 External Leak Small | One-Stage Update | 4 | 2.81e-07 | 1.01e-07 | 2.54e-07 | 5.1e-07 | 2.0079
| TNK1L | Tank 1 External Leak Large | Two-Stage Update | 3 | 4.2e-08 | 1.56e-08 | 3.6e-08 | 7.25e-08 | 2.0139 |  | TK1L | Tank 1 External Leak Large | One-Stage Update | 3 | 2.46e-08 | 7.03e-09 | 2.15e-08 | 4.83e-08 | 2.2465
First Stage Update Using NavyBulkTank_SpillReleaseData In RISKMAN
| RM DIST. | Distribution Type | Mean | 5th | Median | 95th | Error Factor
| TKELSU | One-Stage Update | 5.73e-07 | 3e-07 | 5.44e-07 | 8.87e-07 | 1.6305
| TKELLU | One-Stage Update | 1.71e-08 | 3.43e-09 | 1.41e-08 | 3.71e-08 | 2.6312
Generic Distribution from NUREC CR 6928 In RISKMAN
| RM DIST. | Distribution Type | Mean | 5th | Median | 95th | Error Factor
| TNKELS | Gamma | 3.2e-08 | 1.06e-10 | 1.32e-08 | 1.137e-07 | 8.6136
| TNKELL | Gamma | 2.26e-09 | 1.82e-13 | 4.74e-10 | 9.28e-09 | 19.5781
Generic Distribution from NUREC CR 6928
| Tank (Unpressurized) |  |  | Failure Mode | Distribution Type | Mean | Alpha | Beta | Error Factor
| External Leak Small (1 to 50 gpm.) |  |  | TNK UNPR ELS | Gamma | 3.19e-08 | 0.5 | 15670000 | 8.4
| External Leak Large (> 50 gpm. Small leak times 0.07.) |  |  | TNK UNPR ELL | Gamma | 2.23e-09 | 0.3 | 134400000 | 18.8

## Tank 2
| Date | Tank | Quantity (gallons) | Small / Large | Rate | Type | Detection Method | Mitigation | Cause | Data Source | Comments
| 1947 Oct. | 2 |  | Small |  | JP-5 | telltale | tank emptied |  | EPA-R09-UST-2015-0441-0559 (1).pdf
| 1954 May | 2 |  | Small | 10 gallons in 7 hours | JP-5 |  |  |  | EPA-R09-UST-2015-0441-0559 (1).pdf RH_Tank02_UnverifiedHistory.PDF
| Years | Incidents | Total release (Gallons)
Total: | 65 | 2 | 0
Per Year: |  | 0.030769 | 0
# incidents with sizeable leaks for 20 tanks. |  |  | 0
|  |  | Small Leaks | 2
|  |  | Large Leaks | 0
| Second Stage Update Using RedHill Specific Data for Tank 2 | [9 empty] | First Stage Update Using RedHill Specific Data for Tank 2 (wo the NavyBulkTank_SpillReleaseData update)
| RM DIST. | Failure Mode | Distribution Type | No. Releases | Mean | 5th | Median | 95th | Error Factor |  | RM DIST. | Failure Mode | Distribution Type | No. Releases | Mean | 5th | Median | 95th | Error Factor
| TK2SU | Tank 2 External Leak Small | Two-Stage Update | 2 | 6.81e-07 | 3.74e-07 | 6.48e-07 | 1.03e-06 | 1.5895 |  | TK2S | Tank 2 External Leak Small | One-Stage Update | 2 | 1.56e-07 | 3.43e-08 | 1.31e-07 | 3.31e-07 | 2.5267
| TK2LU | Tank 2 External Leak Large | Two-Stage Update | 0 | 1.71e-08 | 3.41e-09 | 1.41e-08 | 3.69e-08 | 2.617 |  | TK2L | Tank 2 External Leak Large | One-Stage Update | 0 | 2.25e-09 | 1.84e-13 | 4.74e-10 | 9.27e-09 | 19.557

## Tank 3
| Date | Tank | Quantity (gallons) | Small / Large | Rate | Type | Detection Method | Mitigation | Cause | Data Source | Comments
| Years | Incidents | Total release (Gallons)
Total: | 65 | 0 | 0
Per Year: |  | 0 | 0
# incidents with sizeable leaks for 20 tanks. |  |  | 0
|  |  | Small Leaks | 0
|  |  | Large Leaks | 0
| Second Stage Update Using RedHill Specific Data for Tank 3 | [9 empty] | First Stage Update Using RedHill Specific Data for Tank 3 (wo the NavyBulkTank_SpillReleaseData update)
| RM DIST. | Failure Mode | Distribution Type | No. Releases | Mean | 5th | Median | 95th | Error Factor |  | RM DIST. | Failure Mode | Distribution Type | No. Releases | Mean | 5th | Median | 95th | Error Factor
| TK3SU | Tank 3 External Leak Small | Two-Stage Update | 0 | 5.61e-07 | 2.93e-07 | 5.33e-07 | 8.71e-07 | 1.6341 |  | TK3S | Tank 3 External Leak Small | One-Stage Update | 0 | 3.09e-08 | 1.03e-10 | 1.27e-08 | 1.09e-07 | 8.5827
| TK3LU | Tank 3 External Leak Large | Two-Stage Update | 0 | 1.71e-08 | 3.41e-09 | 1.41e-08 | 3.69e-08 | 2.617 |  | TK3L | Tank 3 External Leak Large | One-Stage Update | 0 | 2.25e-09 | 1.84e-13 | 4.74e-10 | 9.27e-09 | 19.557

## Tank 4
| Date | Tank | Quantity (gallons) | Small / Large | Rate | Type | Detection Method | Mitigation | Cause | Data Source | Comments
| Years | Incidents | Total release (Gallons)
Total: | 65 | 0 | 0
Per Year: |  | 0 | 0
# incidents with sizeable leaks for 20 tanks. |  |  | 0
|  |  | Small Leaks | 0
|  |  | Large Leaks | 0
| Second Stage Update Using RedHill Specific Data for Tank 4 | [9 empty] | First Stage Update Using RedHill Specific Data for Tank 4 (wo the NavyBulkTank_SpillReleaseData update)
| RM DIST. | Failure Mode | Distribution Type | No. Releases | Mean | 5th | Median | 95th | Error Factor |  | RM DIST. | Failure Mode | Distribution Type | No. Releases | Mean | 5th | Median | 95th | Error Factor
| TK4SU | Tank 4 External Leak Small | Two-Stage Update | 0 | 5.61e-07 | 2.93e-07 | 5.33e-07 | 8.71e-07 | 1.6341 |  | TK4S | Tank 4 External Leak Small | One-Stage Update | 0 | 3.09e-08 | 1.03e-10 | 1.27e-08 | 1.09e-07 | 8.5827
| TK4LU | Tank 4 External Leak Large | Two-Stage Update | 0 | 1.71e-08 | 3.41e-09 | 1.41e-08 | 3.69e-08 | 2.617 |  | TK4L | Tank 4 External Leak Large | One-Stage Update | 0 | 2.25e-09 | 1.83e-13 | 4.73e-10 | 9.25e-09 | 19.556

## Tank 5
| Date | Tank | Quantity (gallons) | Small / Large | Rate | Type | Detection Method | Mitigation | Cause | Data Source | Comments
| 1965 Mar. | 5 |  | Small | 1 gallon per 1.25 hours | JP-5 |  |  |  | EPA-R09-UST-2015-0441-0559 (1).pdf
| 1972 Feb. | 5 |  | Small | 2 quarts per day | JP-5 | telltale |  |  | EPA-R09-UST-2015-0441-0559 (1).pdf
| 2014 Jan. 13 | 5 | 27000 | Large |  | JP-5 | fuel loss | Fuel transferred to other tanks | After inspection (tests) | EPA-R09-UST-2015-0441-0559 (1).pdf red-hill-aoc-press-release (1).pdf
| Years | Incidents | Total release (Gallons)
Total: | 65 | 3 | 27000
Per Year: |  | 0.046154 | 415.3846
# incidents with sizeable leaks for 20 tanks. |  |  | 1
|  |  | Small Leaks | 2
|  |  | Large Leaks | 1
| Second Stage Update Using RedHill Specific Data for Tank 5 | [9 empty] | First Stage Update Using RedHill Specific Data for Tank 5 (wo the NavyBulkTank_SpillReleaseData update)
| RM DIST. | Failure Mode | Distribution Type | No. Releases | Mean | 5th | Median | 95th | Error Factor |  | RM DIST. | Failure Mode | Distribution Type | No. Releases | Mean | 5th | Median | 95th | Error Factor
| TK5SU | Tank 5 External Leak Small | Two-Stage Update | 2 | 6.81e-07 | 3.74e-07 | 6.48e-07 | 1.03e-06 | 1.5895 |  | TK5S | Tank 5 External Leak Small | One-Stage Update | 2 | 1.56e-07 | 3.43e-08 | 1.31e-07 | 3.31e-07 | 2.5267
| TK5LU | Tank 5 External Leak Large | Two-Stage Update | 1 | 2.46e-08 | 6.72e-09 | 2.12e-08 | 4.89e-08 | 2.3066 |  | TK5L | Tank 5 External Leak Large | One-Stage Update | 1 | 9.7e-09 | 8.23e-10 | 6.99e-09 | 2.51e-08 | 3.5908

## Tank 6
| Date | Tank | Quantity (gallons) | Small / Large | Rate | Type | Detection Method | Mitigation | Cause | Data Source | Comments
| 2002 Apr. | 6 |  | Small |  | JP-5 | taken out of service after a confirmed release |  |  | EPA-R09-UST-2015-0441-0559 (1).pdf
| Years | Incidents | Total release (Gallons)
Total: | 65 | 1 | 0
Per Year: |  | 0.015385 | 0
# incidents with sizeable leaks for 20 tanks. |  |  | 0
|  |  | Small Leaks | 1
|  |  | Large Leaks | 0
| Second Stage Update Using RedHill Specific Data for Tank 6 | [9 empty] | First Stage Update Using RedHill Specific Data for Tank 6 (wo the NavyBulkTank_SpillReleaseData update)
| RM DIST. | Failure Mode | Distribution Type | No. Releases | Mean | 5th | Median | 95th | Error Factor |  | RM DIST. | Failure Mode | Distribution Type | No. Releases | Mean | 5th | Median | 95th | Error Factor
| TK6SU | Tank 6 External Leak Small | Two-Stage Update | 1 | 6.21e-07 | 3.34e-07 | 5.91e-07 | 9.52e-07 | 1.6108 |  | TK6S | Tank 6 External Leak Small | One-Stage Update | 1 | 9.36e-08 | 1.03e-08 | 7.05e-08 | 2.31e-07 | 3.2766
| TK6LU | Tank 6 External Leak Large | Two-Stage Update | 0 | 1.71e-08 | 3.41e-09 | 1.41e-08 | 3.69e-08 | 2.617 |  | TK6L | Tank 6 External Leak Large | One-Stage Update | 0 | 2.25e-09 | 1.83e-13 | 4.73e-10 | 9.25e-09 | 19.556

## Tank 7
| Date | Tank | Quantity (gallons) | Small / Large | Rate | Type | Detection Method | Mitigation | Cause | Data Source | Comments
| 1973 Nov. | 7 |  | Small |  | DFM | telltale | tank emptied |  | EPA-R09-UST-2015-0441-0559 (1).pdf
| 1978 May | 7 |  | Small | significant telltale leak | DFM | telltale | tank emptied |  | EPA-R09-UST-2015-0441-0559 (1).pdf
| 1980 Feb. | 7 | 6505 | Large | rate dropped to< 13 gallons per day below 207 foot fill level | DFM |  |  |  | EPA-R09-UST-2015-0441-0559 (1).pdf
| Years | Incidents | Total release (Gallons)
Total: | 65 | 3 | 6505
Per Year: |  | 0.046154 | 100.0769
# incidents with sizeable leaks for 20 tanks. |  |  | 1
|  |  | Small Leaks | 2
|  |  | Large Leaks | 1
| Second Stage Update Using RedHill Specific Data for Tank 7 | [9 empty] | First Stage Update Using RedHill Specific Data for Tank 7 (wo the NavyBulkTank_SpillReleaseData update)
| RM DIST. | Failure Mode | Distribution Type | No. Releases | Mean | 5th | Median | 95th | Error Factor |  | RM DIST. | Failure Mode | Distribution Type | No. Releases | Mean | 5th | Median | 95th | Error Factor
| TK7SU | Tank 7 External Leak Small | Two-Stage Update | 2 | 6.81e-07 | 3.74e-07 | 6.48e-07 | 1.03e-06 | 1.5895 |  | TK7S | Tank 7 External Leak Small | One-Stage Update | 2 | 1.56e-07 | 3.43e-08 | 1.31e-07 | 3.31e-07 | 2.5267
| TK7LU | Tank 7 External Leak Large | Two-Stage Update | 1 | 2.46e-08 | 6.72e-09 | 2.12e-08 | 4.89e-08 | 2.3066 |  | TK7L | Tank 7 External Leak Large | One-Stage Update | 1 | 9.7e-09 | 8.23e-10 | 6.99e-09 | 2.51e-08 | 3.5908

## Tank 8
| Date | Tank | Quantity (gallons) | Small / Large | Rate | Type | Detection Method | Mitigation | Cause | Data Source | Comments
| Years | Incidents | Total release (Gallons)
Total: | 65 | 0 | 0
Per Year: |  | 0 | 0
# incidents with sizeable leaks for 20 tanks. |  |  | 0
|  |  | Small Leaks | 0
|  |  | Large Leaks | 0
| Second Stage Update Using RedHill Specific Data for Tank 1 | [9 empty] | First Stage Update Using RedHill Specific Data for Tank 8 (wo the NavyBulkTank_SpillReleaseData update)
| RM DIST. | Failure Mode | Distribution Type | No. Releases | Mean | 5th | Median | 95th | Error Factor |  | RM DIST. | Failure Mode | Distribution Type | No. Releases | Mean | 5th | Median | 95th | Error Factor
| TK8SU | Tank 8 External Leak Small | Two-Stage Update | 0 | 5.61e-07 | 2.93e-07 | 5.33e-07 | 8.71e-07 | 1.6341 |  | TK8S | Tank 8 External Leak Small | One-Stage Update | 0 | 3.09e-08 | 1.03e-10 | 1.27e-08 | 1.09e-07 | 8.5827
| TK8LU | Tank 8 External Leak Large | Two-Stage Update | 0 | 1.71e-08 | 3.41e-09 | 1.41e-08 | 3.69e-08 | 2.617 |  | TK8L | Tank 8 External Leak Large | One-Stage Update | 0 | 2.25e-09 | 1.84e-13 | 4.74e-10 | 9.27e-09 | 19.557

## Tank 9
| Date | Tank | Quantity (gallons) | Small / Large | Rate | Type | Detection Method | Mitigation | Cause | Data Source | Comments
| 1958 Apr. | 9 | 1500 | Small |  | DFM | telltale |  |  | EPA-R09-UST-2015-0441-0559 (1).pdf
| 1978 Jul. | 9 |  | Small | 4.5 to 17.9 gallons/day | DFM | Leak test | no documentation of any actions taken to mitigate | after the repair project | EPA-R09-UST-2015-0441-0559 (1).pdf
| Years | Incidents | Total release (Gallons)
Total: | 65 | 2 | 1500
Per Year: |  | 0.030769 | 23.0769
# incidents with sizeable leaks for 20 tanks. |  |  | 1
|  |  | Small Leaks | 2
|  |  | Large Leaks | 0
| Second Stage Update Using RedHill Specific Data for Tank 9 | [9 empty] | First Stage Update Using RedHill Specific Data for Tank 9 (wo the NavyBulkTank_SpillReleaseData update)
| RM DIST. | Failure Mode | Distribution Type | No. Releases | Mean | 5th | Median | 95th | Error Factor |  | RM DIST. | Failure Mode | Distribution Type | No. Releases | Mean | 5th | Median | 95th | Error Factor
| TK9SU | Tank 9 External Leak Small | Two-Stage Update | 2 | 6.81e-07 | 3.74e-07 | 6.48e-07 | 1.03e-06 | 1.5895 |  | TK9S | Tank 9 External Leak Small | One-Stage Update | 2 | 1.56e-07 | 3.43e-08 | 1.31e-07 | 3.31e-07 | 2.5267
| TK9LU | Tank 9 External Leak Large | Two-Stage Update | 0 | 1.71e-08 | 3.41e-09 | 1.41e-08 | 3.69e-08 | 2.617 |  | TK9L | Tank 9 External Leak Large | One-Stage Update | 0 | 2.25e-09 | 1.84e-13 | 4.74e-10 | 9.27e-09 | 19.557

## Tank 10
| Date | Tank | Quantity (gallons) | Small / Large | Rate | Type | Detection Method | Mitigation | Cause | Data Source | Comments
| 1973 Jan. | 10 |  | Small |  | DFM | leak suspected | tank emptied |  | EPA-R09-UST-2015-0441-0559 (1).pdf
| 1976 Apr. | 10 |  | Small |  | DFM | telltale | tank emptied |  | EPA-R09-UST-2015-0441-0559 (1).pdf
| 1981 Jan. | 10 |  | Small | severe leak near the top of the tank (between the 235- and 242-foot level) | DFM |  | tank emptied |  | EPA-R09-UST-2015-0441-0559 (1).pdf
| Years | Incidents | Total release (Gallons)
Total: | 65 | 3 | 0
Per Year: |  | 0.046154 | 0
# incidents with sizeable leaks for 20 tanks. |  |  | 0
|  |  | Small Leaks | 3
|  |  | Large Leaks | 0
| Second Stage Update Using RedHill Specific Data for Tank 10 | [9 empty] | First Stage Update Using RedHill Specific Data for Tank 10 (wo the NavyBulkTank_SpillReleaseData update)
| RM DIST. | Failure Mode | Distribution Type | No. Releases | Mean | 5th | Median | 95th | Error Factor |  | RM DIST. | Failure Mode | Distribution Type | No. Releases | Mean | 5th | Median | 95th | Error Factor
| TK10SU | Tank 10 External Leak Small | Two-Stage Update | 3 | 7.43e-07 | 4.21e-07 | 7.05e-07 | 1.11e-06 | 1.5745 |  | TK10S | Tank 10 External Leak Small | One-Stage Update | 3 | 2.18 | 6.54e-08 | 1.92e-07 | 4.22e-07 | 2.1979
| TK10LU | Tank 10 External Leak Large | Two-Stage Update | 0 | 1.71e-08 | 3.41e-09 | 1.41e-08 | 3.69e-08 | 2.617 |  | TK10L | Tank 10 External Leak Large | One-Stage Update | 0 | 2.25e-09 | 1.84e-13 | 4.74e-10 | 9.27e-09 | 19.557

## Tank 11
| Date | Tank | Quantity (gallons) | Small / Large | Rate | Type | Detection Method | Mitigation | Cause | Data Source | Comments
| 1980 Aug. | 11 | 15000 | Large | 10,000 to 20,000 gallons 1,000 to 1,500 gallons per day | DFM |  | emptied and repaired |  | EPA-R09-UST-2015-0441-0559 (1).pdf
| Years | Incidents | Total release (Gallons)
Total: | 65 | 1 | 15000
Per Year: |  | 0.015385 | 230.7692
# incidents with sizeable leaks for 20 tanks. |  |  | 1
|  |  | Small Leaks | 0
|  |  | Large Leaks | 1
| Second Stage Update Using RedHill Specific Data for Tank 11 | [9 empty] | First Stage Update Using RedHill Specific Data for Tank 11 (wo the NavyBulkTank_SpillReleaseData update)
| RM DIST. | Failure Mode | Distribution Type | No. Releases | Mean | 5th | Median | 95th | Error Factor |  | RM DIST. | Failure Mode | Distribution Type | No. Releases | Mean | 5th | Median | 95th | Error Factor
| TK11SU | Tank 11 External Leak Small | Two-Stage Update | 0 | 5.61e-07 | 2.93e-07 | 5.33e-07 | 8.71e-07 | 1.6341 |  | TK11S | Tank 11 External Leak Small | One-Stage Update | 0 | 3.09e-08 | 1.03e-10 | 1.27e-08 | 1.09e-07 | 8.5827
| TK11LU | Tank 11 External Leak Large | Two-Stage Update | 1 | 2.46e-08 | 6.72e-09 | 2.12e-08 | 4.89e-08 | 2.3066 |  | TK11L | Tank 11 External Leak Large | One-Stage Update | 1 | 9.7e-09 | 8.23e-10 | 6.99e-09 | 2.51e-08 | 3.5908

## Tank 12
| Date | Tank | Quantity (gallons) | Small / Large | Rate | Type | Detection Method | Mitigation | Cause | Data Source | Comments
| 1964 Jan. | 12 |  | Small |  | DFM |  |  | dome section leak identified | EPA-R09-UST-2015-0441-0559 (1).pdf
| 1973 Mar. | 12 |  | Small |  | DFM | suspected leak | tank emptied |  | EPA-R09-UST-2015-0441-0559 (1).pdf
| 1981 Feb. | 12 |  | Large | 1,440 gallons per day at the 100-foot level | DFM |  |  | after repairs | EPA-R09-UST-2015-0441-0559 (1).pdf
| Years | Incidents | Total release (Gallons)
Total: | 65 | 3 | 0
Per Year: |  | 0.046154 | 0
# incidents with sizeable leaks for 20 tanks. |  |  | 0
|  |  | Small Leaks | 2
|  |  | Large Leaks | 1
| Second Stage Update Using RedHill Specific Data for Tank 12 | [9 empty] | First Stage Update Using RedHill Specific Data for Tank 12 (wo the NavyBulkTank_SpillReleaseData update)
| RM DIST. | Failure Mode | Distribution Type | No. Releases | Mean | 5th | Median | 95th | Error Factor |  | RM DIST. | Failure Mode | Distribution Type | No. Releases | Mean | 5th | Median | 95th | Error Factor
| TK12SU | Tank 5 External Leak Small | Two-Stage Update | 2 | 6.81e-07 | 3.74e-07 | 6.48e-07 | 1.03e-06 | 1.5895 |  | TK12S | Tank 5 External Leak Small | One-Stage Update | 2 | 1.56e-07 | 3.43e-08 | 1.31e-07 | 3.31e-07 | 2.5267
| TK12LU | Tank 5 External Leak Large | Two-Stage Update | 1 | 2.46e-08 | 6.72e-09 | 2.12e-08 | 4.89e-08 | 2.3066 |  | TK12L | Tank 5 External Leak Large | One-Stage Update | 1 | 9.7e-09 | 8.23e-10 | 6.99e-09 | 2.51e-08 | 3.5908

## Tank 13
| Date | Tank | Quantity (gallons) | Small / Large | Rate | Type | Detection Method | Mitigation | Cause | Data Source | Comments
| 1976 May | 13 |  | Small |  | DFM | reported as leaking |  |  | EPA-R09-UST-2015-0441-0559 (1).pdf
| Years | Incidents | Total release (Gallons)
Total: | 65 | 1 | 0
Per Year: |  | 0.015385 | 0
# incidents with sizeable leaks for 20 tanks. |  |  | 0
|  |  | Small Leaks | 1
|  |  | Large Leaks | 0
| Second Stage Update Using RedHill Specific Data for Tank 13 | [9 empty] | First Stage Update Using RedHill Specific Data for Tank 13 (wo the NavyBulkTank_SpillReleaseData update)
| RM DIST. | Failure Mode | Distribution Type | No. Releases | Mean | 5th | Median | 95th | Error Factor |  | RM DIST. | Failure Mode | Distribution Type | No. Releases | Mean | 5th | Median | 95th | Error Factor
| TK13SU | Tank 13 External Leak Small | Two-Stage Update | 1 | 6.21e-07 | 3.34e-07 | 5.91e-07 | 9.52e-07 | 1.6108 |  | TK13S | Tank 13 External Leak Small | One-Stage Update | 1 | 9.36e-08 | 1.03e-08 | 7.05e-08 | 2.31e-07 | 3.2766
| TK13LU | Tank 13 External Leak Large | Two-Stage Update | 0 | 1.71e-08 | 3.41e-09 | 1.41e-08 | 3.69e-08 | 2.617 |  | TK13L | Tank 13 External Leak Large | One-Stage Update | 0 | 2.25e-09 | 1.83e-13 | 4.73e-10 | 9.25e-09 | 19.556

## Tank 14
| Date | Tank | Quantity (gallons) | Small / Large | Rate | Type | Detection Method | Mitigation | Cause | Data Source | Comments
| Years | Incidents | Total release (Gallons)
Total: | 65 | 0 | 0
Per Year: |  | 0 | 0
# incidents with sizeable leaks for 20 tanks. |  |  | 0
|  |  | Small Leaks | 0
|  |  | Large Leaks | 0
| Second Stage Update Using RedHill Specific Data for Tank 14 | [9 empty] | First Stage Update Using RedHill Specific Data for Tank 14 (wo the NavyBulkTank_SpillReleaseData update)
| RM DIST. | Failure Mode | Distribution Type | No. Releases | Mean | 5th | Median | 95th | Error Factor |  | RM DIST. | Failure Mode | Distribution Type | No. Releases | Mean | 5th | Median | 95th | Error Factor
| TK14SU | Tank 14 External Leak Small | Two-Stage Update | 0 | 5.61e-07 | 2.93e-07 | 5.33e-07 | 8.71e-07 | 1.6341 |  | TK14S | Tank 14 External Leak Small | One-Stage Update | 0 | 3.09e-08 | 1.03e-10 | 1.27e-08 | 1.09e-07 | 8.5827
| TK14LU | Tank 14 External Leak Large | Two-Stage Update | 0 | 1.71e-08 | 3.41e-09 | 1.41e-08 | 3.69e-08 | 2.617 |  | TK14L | Tank 14 External Leak Large | One-Stage Update | 0 | 2.25e-09 | 1.84e-13 | 4.74e-10 | 9.27e-09 | 19.557

## Tank 15
| Date | Tank | Quantity (gallons) | Small / Large | Rate | Type | Detection Method | Mitigation | Cause | Data Source | Comments
| 1981 Jul. | 15 |  | Small | leaking badly | DFM |  |  | after tank repair and lining | EPA-R09-UST-2015-0441-0559 (1).pdf
| Years | Incidents | Total release (Gallons)
Total: | 65 | 1 | 0
Per Year: |  | 0.015385 | 0
# incidents with sizeable leaks for 20 tanks. |  |  | 0
|  |  | Small Leaks | 1
|  |  | Large Leaks | 0
| Second Stage Update Using RedHill Specific Data for Tank 15 | [9 empty] | First Stage Update Using RedHill Specific Data for Tank 15 (wo the NavyBulkTank_SpillReleaseData update)
| RM DIST. | Failure Mode | Distribution Type | No. Releases | Mean | 5th | Median | 95th | Error Factor |  | RM DIST. | Failure Mode | Distribution Type | No. Releases | Mean | 5th | Median | 95th | Error Factor
| TK15SU | Tank 15 External Leak Small | Two-Stage Update | 1 | 6.21e-07 | 3.34e-07 | 5.91e-07 | 9.52e-07 | 1.6108 |  | TK15S | Tank 15 External Leak Small | One-Stage Update | 1 | 9.36e-08 | 1.03e-08 | 7.05e-08 | 2.31e-07 | 3.2766
| TK15LU | Tank 15 External Leak Large | Two-Stage Update | 0 | 1.71e-08 | 3.41e-09 | 1.41e-08 | 3.69e-08 | 2.617 |  | TK15L | Tank 15 External Leak Large | One-Stage Update | 0 | 2.25e-09 | 1.83e-13 | 4.73e-10 | 9.25e-09 | 19.556

## Tank 16
| Date | Tank | Quantity (gallons) | Small / Large | Rate | Type | Detection Method | Mitigation | Cause | Data Source | Comments
| 1948 Jul. | 16 | 11000 | Large |  |  | telltale | tank emptied |  | EPA-R09-UST-2015-0441-0559 (1).pdf
| 1949 Dec. | 16 | 18000 | Large |  |  | telltale |  |  | EPA-R09-UST-2015-0441-0559 (1).pdf
| 1973 May | 16 |  | Small | 1 drop per 20 seconds |  | telltale |  |  | EPA-R09-UST-2015-0441-0559 (1).pdf
| 1981 | 16 |  | Small | leaking badly |  |  |  | after repairs when filled to 242-foot level | EPA-R09-UST-2015-0441-0559 (1).pdf
| 1981 Oct. | 16 |  | Small | leaking badly |  |  |  | after repairs and lining | EPA-R09-UST-2015-0441-0559 (1).pdf
| 1998 Oct. | 16 | 1469 | Large | 71 gal/day (over 30.7 days) |  | Tank level drop; petroleum found under base of tank | tank emptied |  | EPA-R09-UST-2015-0441-0559 (1).pdf
| Years | Incidents | Total release (Gallons)
Total: | 65 | 6 | 30469
Per Year: |  | 0.092308 | 468.7538
# incidents with sizeable leaks for 20 tanks. |  |  | 3
|  |  | Small Leaks | 3
|  |  | Large Leaks | 3
| Second Stage Update Using RedHill Specific Data for Tank 16 | [9 empty] | First Stage Update Using RedHill Specific Data for Tank 16 (wo the NavyBulkTank_SpillReleaseData update)
| RM DIST. | Failure Mode | Distribution Type | No. Releases | Mean | 5th | Median | 95th | Error Factor |  | RM DIST. | Failure Mode | Distribution Type | No. Releases | Mean | 5th | Median | 95th | Error Factor
| TK16SU | Tank 16 External Leak Small | Two-Stage Update | 3 | 7.43e-07 | 4.21e-07 | 7.05e-07 | 1.11e-06 | 1.5745 |  | TK16S | Tank 16 External Leak Small | One-Stage Update | 3 | 2.18 | 6.54e-08 | 1.92e-07 | 4.22e-07 | 2.1979
| TK16LU | Tank 16 External Leak Large | Two-Stage Update | 3 | 4.2e-08 | 1.56e-08 | 3.6e-08 | 7.25e-08 | 2.0139 |  | TK16L | Tank 16 External Leak Large | One-Stage Update | 3 | 2.46e-08 | 7.03e-09 | 2.15e-08 | 4.83e-08 | 2.2465

## Tank 17
| Date | Tank | Quantity (gallons) | Small / Large | Rate | Type | Detection Method | Mitigation | Cause | Data Source | Comments
| 1969 Jun. | 17 |  | Small | gallon per 1.5 minutes | JP-5 | telltale |  |  | EPA-R09-UST-2015-0441-0559 (1).pdf
| 1975 Jan. | 17 |  | Small |  | JP-5 | telltale |  |  | EPA-R09-UST-2015-0441-0559 (1).pdf
| Years | Incidents | Total release (Gallons)
Total: | 65 | 2 | 0
Per Year: |  | 0.030769 | 0
# incidents with sizeable leaks for 20 tanks. |  |  | 0
|  |  | Small Leaks | 2
|  |  | Large Leaks | 0
| Second Stage Update Using RedHill Specific Data for Tank 17 | [9 empty] | First Stage Update Using RedHill Specific Data for Tank 17 (wo the NavyBulkTank_SpillReleaseData update)
| RM DIST. | Failure Mode | Distribution Type | No. Releases | Mean | 5th | Median | 95th | Error Factor |  | RM DIST. | Failure Mode | Distribution Type | No. Releases | Mean | 5th | Median | 95th | Error Factor
| TK17SU | Tank 17 External Leak Small | Two-Stage Update | 2 | 6.81e-07 | 3.74e-07 | 6.48e-07 | 1.03e-06 | 1.5895 |  | TK17S | Tank 17 External Leak Small | One-Stage Update | 2 | 1.56e-07 | 3.43e-08 | 1.31e-07 | 3.31e-07 | 2.5267
| TK17LU | Tank 17 External Leak Large | Two-Stage Update | 0 | 1.71e-08 | 3.41e-09 | 1.41e-08 | 3.69e-08 | 2.617 |  | TK17L | Tank 17 External Leak Large | One-Stage Update | 0 | 2.25e-09 | 1.84e-13 | 4.74e-10 | 9.27e-09 | 19.557

## Tank 18
| Date | Tank | Quantity (gallons) | Small / Large | Rate | Type | Detection Method | Mitigation | Cause | Data Source | Comments
| Years | Incidents | Total release (Gallons)
Total: | 65 | 0 | 0
Per Year: |  | 0 | 0
# incidents with sizeable leaks for 20 tanks. |  |  | 0
|  |  | Small Leaks | 0
|  |  | Large Leaks | 0
| Second Stage Update Using RedHill Specific Data for Tank 18 | [9 empty] | First Stage Update Using RedHill Specific Data for Tank 18 (wo the NavyBulkTank_SpillReleaseData update)
| RM DIST. | Failure Mode | Distribution Type | No. Releases | Mean | 5th | Median | 95th | Error Factor |  | RM DIST. | Failure Mode | Distribution Type | No. Releases | Mean | 5th | Median | 95th | Error Factor
| TK18SU | Tank 18 External Leak Small | Two-Stage Update | 0 | 5.61e-07 | 2.93e-07 | 5.33e-07 | 8.71e-07 | 1.6341 |  | TK18S | Tank 18 External Leak Small | One-Stage Update | 0 | 3.09e-08 | 1.03e-10 | 1.27e-08 | 1.09e-07 | 8.5827
| TK18LU | Tank 18 External Leak Large | Two-Stage Update | 0 | 1.71e-08 | 3.41e-09 | 1.41e-08 | 3.69e-08 | 2.617 |  | TK18L | Tank 18 External Leak Large | One-Stage Update | 0 | 2.25e-09 | 1.84e-13 | 4.74e-10 | 9.27e-09 | 19.557

## Tank 19
| Date | Tank | Quantity (gallons) | Small / Large | Rate | Type | Detection Method | Mitigation | Cause | Data Source | Comments
| 1964 Jun. | 19 |  | Small | 5 mL/hr. | JP-5 | telltale |  | weld leak discovered, | EPA-R09-UST-2015-0441-0559 (1).pdf
| 1998 | 19 |  | Small |  | JP-5 | back seepage |  |  | EPA-R09-UST-2015-0441-0559 (1).pdf
| Years | Incidents | Total release (Gallons)
Total: | 65 | 2 | 0
Per Year: |  | 0.030769 | 0
# incidents with sizeable leaks for 20 tanks. |  |  | 0
|  |  | Small Leaks | 2
|  |  | Large Leaks | 0
| Second Stage Update Using RedHill Specific Data for Tank 19 | [9 empty] | First Stage Update Using RedHill Specific Data for Tank 19 (wo the NavyBulkTank_SpillReleaseData update)
| RM DIST. | Failure Mode | Distribution Type | No. Releases | Mean | 5th | Median | 95th | Error Factor |  | RM DIST. | Failure Mode | Distribution Type | No. Releases | Mean | 5th | Median | 95th | Error Factor
| TK19SU | Tank 19 External Leak Small | Two-Stage Update | 2 | 6.81e-07 | 3.74e-07 | 6.48e-07 | 1.03e-06 | 1.5895 |  | TK19S | Tank 19 External Leak Small | One-Stage Update | 2 | 1.56e-07 | 3.43e-08 | 1.31e-07 | 3.31e-07 | 2.5267
| TK19LU | Tank 19 External Leak Large | Two-Stage Update | 0 | 1.71e-08 | 3.41e-09 | 1.41e-08 | 3.69e-08 | 2.617 |  | TK19L | Tank 19 External Leak Large | One-Stage Update | 0 | 2.25e-09 | 1.84e-13 | 4.74e-10 | 9.27e-09 | 19.557

## Tank 20
| Date | Tank | Quantity (gallons) | Small / Large | Rate | Type | Detection Method | Mitigation | Cause | Data Source | Comments
| Years | Incidents | Total release (Gallons)
Total: | 65 | 0
Per Year: |  | 0
# incidents with sizeable leaks for 20 tanks.
|  |  | Small Leaks | 0
|  |  | Large Leaks | 0
| Second Stage Update Using RedHill Specific Data for Tank 20 | [9 empty] | First Stage Update Using RedHill Specific Data for Tank 20 (wo the NavyBulkTank_SpillReleaseData update)
| RM DIST. | Failure Mode | Distribution Type | No. Releases | Mean | 5th | Median | 95th | Range Factor |  | RM DIST. | Failure Mode | Distribution Type | No. Releases | Mean | 5th | Median | 95th | Error Factor
| TK20SU | Tank 20 External Leak Small | Two-Stage Update | 0 | 5.61e-07 | 2.93e-07 | 5.33e-07 | 8.71e-07 | 1.6341 |  | TK20S | Tank 20 External Leak Small | One-Stage Update | 0 | 3.09e-08 | 1.03e-10 | 1.27e-08 | 1.09e-07 | 8.5827
| TK20LU | Tank 20 External Leak Large | Two-Stage Update | 0 | 1.71e-08 | 3.41e-09 | 1.41e-08 | 3.69e-08 | 2.617 |  | TK20L | Tank 20 External Leak Large | One-Stage Update | 0 | 2.25e-09 | 1.84e-13 | 4.74e-10 | 9.27e-09 | 19.557

## Table 5.4-1 Response Event Data
Component Index | System/Component (From P&ID) | Failure Mode | Component Type Link (6928) | Failure Mode ID | Mean Failure Rate | Failure Rate Units | Error Factor (95th/50th)
1 | Ball Valve | Motor-Operated Valve Fail to Control | MOV | FC | 3e-06 | h | 18.8
1 | Ball Valve | Motor-Operated Valve Fail to Open or Close | MOV | FTO/C | 0.00107 | d | 3.6
1 | Ball Valve | Motor-Operated Valve Spurious Operation | MOV | SO | 4.45e-08 | h | 8.4
1 | Ball Valve | Motor-Operated Valve External Leak Small | MOV | ELS | 1.41e-08 | h | 8.4
1 | Ball Valve | Motor-Operated Valve External Leak Large | MOV | ELL | 9.84e-10 | h | 18.8
1 | Ball Valve | Motor-Operated Valve Internal Leak Small | MOV | ILS | 1.67e-07 | h | 10.2
1 | Ball Valve | Motor-Operated Valve Internal Leak Large | MOV | ILL | 3.34e-09 | h | 18.8
2 | Butterfly Valve | Motor-Operated Valve Fail to Control | MOV | FC | 3e-06 | h | 18.8
2 | Butterfly Valve | Motor-Operated Valve Fail to Open or Close | MOV | FTO/C | 0.00107 | d | 3.6
2 | Butterfly Valve | Motor-Operated Valve Spurious Operation | MOV | SO | 4.45e-08 | h | 8.4
2 | Butterfly Valve | Motor-Operated Valve External Leak Small | MOV | ELS | 1.41e-08 | h | 8.4
2 | Butterfly Valve | Motor-Operated Valve External Leak Large | MOV | ELL | 9.84e-10 | h | 18.8
2 | Butterfly Valve | Motor-Operated Valve Internal Leak Small | MOV | ILS | 1.67e-07 | h | 10.2
2 | Butterfly Valve | Motor-Operated Valve Internal Leak Large | MOV | ILL | 3.34e-09 | h | 18.8
3 | Check Valve | Check Valve Fail to Close | CKV | FTC | 0.000104 | d | 8.4
3 | Check Valve | Check Valve Fail to Open | CKV | FTO | 1.3e-05 | d | 8.4
3 | Check Valve | Check Valve External Leak Small | CKV | ELS | 2.94e-08 | h | 8.4
3 | Check Valve | Check Valve External Leak Large | CKV | ELL | 2.06e-09 | h | 18.8
3 | Check Valve | Check Valve Internal Leak Small | CKV | ILS | 1.48e-06 | h | 18.8
3 | Check Valve | Check Valve Internal Leak Large | CKV | ILL | 2.96e-08 | h | 18.8
4 | Gate Valve | Motor-Operated Valve Fail to Control | MOV | FC | 3e-06 | h | 18.8
4 | Gate Valve | Motor-Operated Valve Fail to Open or Close | MOV | FTO/C | 0.00107 | d | 3.6
4 | Gate Valve | Motor-Operated Valve Spurious Operation | MOV | SO | 4.45e-08 | h | 8.4
4 | Gate Valve | Motor-Operated Valve External Leak Small | MOV | ELS | 1.41e-08 | h | 8.4
4 | Gate Valve | Motor-Operated Valve External Leak Large | MOV | ELL | 9.84e-10 | h | 18.8
4 | Gate Valve | Motor-Operated Valve Internal Leak Small | MOV | ILS | 1.67e-07 | h | 10.2
4 | Gate Valve | Motor-Operated Valve Internal Leak Large | MOV | ILL | 3.34e-09 | h | 18.8
5 | Globe Valve | Motor-Operated Valve Fail to Control | MOV | FC | 3e-06 | h | 18.8
5 | Globe Valve | Motor-Operated Valve Fail to Open or Close | MOV | FTO/C | 0.00107 | d | 3.6
5 | Globe Valve | Motor-Operated Valve Spurious Operation | MOV | SO | 4.45e-08 | h | 8.4
5 | Globe Valve | Motor-Operated Valve External Leak Small | MOV | ELS | 1.41e-08 | h | 8.4
5 | Globe Valve | Motor-Operated Valve External Leak Large | MOV | ELL | 9.84e-10 | h | 18.8
5 | Globe Valve | Motor-Operated Valve Internal Leak Small | MOV | ILS | 1.67e-07 | h | 10.2
5 | Globe Valve | Motor-Operated Valve Internal Leak Large | MOV | ILL | 3.34e-09 | h | 18.8
6 | Plug Valve | Manual Valve Fail to Open or Close | XVM | FTO/C | 0.000743 | d | 8.4
6 | Plug Valve | Manual Valve Plug | XVM | PLG | 6.36e-09 | h | 8.4
6 | Plug Valve | Manual Valve External Leak Small | XVM | ELS | 4.46e-08 | h | 8.4
6 | Plug Valve | Manual Valve External Leak Large | XVM | ELL | 3.12e-09 | h | 18.8
6 | Plug Valve | Manual Valve Internal Leak Small | XVM | ILS | 6.67e-08 | h | 8.4
6 | Plug Valve | Manual Valve Internal Leak Large | XVM | ILL | 1.33e-09 | h | 18.8
7 | Double Block and Bleed Valve | Manual Valve Fail to Open or Close | XVM | FTO/C | 0.000743 | d | 8.4
7 | Double Block and Bleed Valve | Manual Valve Plug | XVM | PLG | 6.36e-09 | h | 8.4
7 | Double Block and Bleed Valve | Manual Valve External Leak Small | XVM | ELS | 4.46e-08 | h | 8.4
7 | Double Block and Bleed Valve | Manual Valve External Leak Large | XVM | ELL | 3.12e-09 | h | 18.8
7 | Double Block and Bleed Valve | Manual Valve Internal Leak Small | XVM | ILS | 6.67e-08 | h | 8.4
7 | Double Block and Bleed Valve | Manual Valve Internal Leak Large | XVM | ILL | 1.33e-09 | h | 18.8
8 | Flow Control Valve | Motor-Operated Valve Fail to Control | MOV | FC | 3e-06 | h | 18.8
8 | Flow Control Valve | Motor-Operated Valve Fail to Open or Close | MOV | FTO/C | 0.00107 | d | 3.6
8 | Flow Control Valve | Motor-Operated Valve Spurious Operation | MOV | SO | 4.45e-08 | h | 8.4
8 | Flow Control Valve | Motor-Operated Valve External Leak Small | MOV | ELS | 1.41e-08 | h | 8.4
8 | Flow Control Valve | Motor-Operated Valve External Leak Large | MOV | ELL | 9.84e-10 | h | 18.8
8 | Flow Control Valve | Motor-Operated Valve Internal Leak Small | MOV | ILS | 1.67e-07 | h | 10.2
8 | Flow Control Valve | Motor-Operated Valve Internal Leak Large | MOV | ILL | 3.34e-09 | h | 18.8
9 | Four Way Double Block and Bleed Valve | Manual Valve Fail to Open or Close | XVM | FTO/C | 0.000743 | d | 8.4
9 | Four Way Double Block and Bleed Valve | Manual Valve Plug | XVM | PLG | 6.36e-09 | h | 8.4
9 | Four Way Double Block and Bleed Valve | Manual Valve External Leak Small | XVM | ELS | 4.46e-08 | h | 8.4
9 | Four Way Double Block and Bleed Valve | Manual Valve External Leak Large | XVM | ELL | 3.12e-09 | h | 18.8
9 | Four Way Double Block and Bleed Valve | Manual Valve Internal Leak Small | XVM | ILS | 6.67e-08 | h | 8.4
9 | Four Way Double Block and Bleed Valve | Manual Valve Internal Leak Large | XVM | ILL | 1.33e-09 | h | 18.8
10 | Pressure Relief or Safety Valve | Safety Relief Valve Fail to Close | SRV | FTC | 0.000795 | d | 8.4
10 | Pressure Relief or Safety Valve | Safety Relief Valve Fail to Open | SRV | FTO | 0.00771 | d | 18.5
10 | Pressure Relief or Safety Valve | Safety Relief Valve Spurious Operation | SRV | SO | 5.08e-07 | h | 18.8
10 | Pressure Relief or Safety Valve | Safety Relief Valve Fail to Close (Passing Liquid) | SRV | FTCL | 0.1 | d | 7
11 | Strainer - Basket Type | Strainer Plug | STR | PLG | 7.38e-06 | h | 18.8
12 | Filter | Filter Plug (Clean Water System) | FLT | PLG | 9.86e-08 | h | 8.4
13 | Filter/Seperator (or Flow Switch) | Manual Switch Fail to Open or Close | FLT for Filter; MSW for Switch | FTO/C | 0.000126 | d | 8.4
14 | Relaxation Tank | Tank Unpressurized External Leak Small | TNK UNPR | ELS | 3.19e-08 | h | 8.4
14 | Relaxation Tank | Tank Unpressurized External Leak Large | TNK UNPR | ELL | 2.23e-09 | h | 18.8
15 | Expansion Joint | Piping Non-Service Water System External Leak Small | PIPE OTHER | ELS | 2.53e-10 | h-ft | 8.4
15 | Expansion Joint | Piping Non-Service Water System External Leak Large | PIPE OTHER | ELL | 2.53e-11 | h-ft | 18.8
16 | Flexible Hose | Piping Non-Service Water System External Leak Small | PIPE OTHER | ELS | 2.53e-10 | h-ft | 8.4
16 | Flexible Hose | Piping Non-Service Water System External Leak Large | PIPE OTHER | ELL | 2.53e-11 | h-ft | 18.8
17 | Conservation Vent / Flame Arrestor | Hydraulic-Operated Damper Fail to Open or Close | HOD | FTO/C | 0.00261 | d | 18.7
17 | Conservation Vent / Flame Arrestor | Hydraulic-Operated Damper Spurious Operation | HOD | SO | 3.03e-07 | h | 8.4
18 | Equipment Drain Funnel | Piping Non-Service Water System External Leak Small | PIPE OTHER | ELS | 2.53e-10 | h-ft | 8.4
18 | Equipment Drain Funnel | Piping Non-Service Water System External Leak Large | PIPE OTHER | ELL | 2.53e-11 | h-ft | 18.8
19 | Slip Blind, Closed | Piping Non-Service Water System External Leak Small | PIPE OTHER | ELS | 2.53e-10 | h-ft | 8.4
19 | Slip Blind, Closed | Piping Non-Service Water System External Leak Large | PIPE OTHER | ELL | 2.53e-11 | h-ft | 18.8
20 | Slip Blind, Open | Piping Non-Service Water System External Leak Small | PIPE OTHER | ELS | 2.53e-10 | h-ft | 8.4
20 | Slip Blind, Open | Piping Non-Service Water System External Leak Large | PIPE OTHER | ELL | 2.53e-11 | h-ft | 18.8
21 | Spectacle Blind, Closed | Piping Non-Service Water System External Leak Small | PIPE OTHER | ELS | 2.53e-10 | h-ft | 8.4
21 | Spectacle Blind, Closed | Piping Non-Service Water System External Leak Large | PIPE OTHER | ELL | 2.53e-11 | h-ft | 18.8
22 | Spectacle Blind, Open | Piping Non-Service Water System External Leak Small | PIPE OTHER | ELS | 2.53e-10 | h-ft | 8.4
22 | Spectacle Blind, Open | Piping Non-Service Water System External Leak Large | PIPE OTHER | ELL | 2.53e-11 | h-ft | 18.8
23 | Blind Flange | Piping Non-Service Water System External Leak Small | PIPE OTHER | ELS | 2.53e-10 | h-ft | 8.4
23 | Blind Flange | Piping Non-Service Water System External Leak Large | PIPE OTHER | ELL | 2.53e-11 | h-ft | 18.8
24 | BW Capped Pipe | Piping Non-Service Water System External Leak Small | PIPE OTHER | ELS | 2.53e-10 | h-ft | 8.4
24 | BW Capped Pipe | Piping Non-Service Water System External Leak Large | PIPE OTHER | ELL | 2.53e-11 | h-ft | 18.8
25 | Capped Pipe | Piping Non-Service Water System External Leak Small | PIPE OTHER | ELS | 2.53e-10 | h-ft | 8.4
25 | Capped Pipe | Piping Non-Service Water System External Leak Large | PIPE OTHER | ELL | 2.53e-11 | h-ft | 18.8
26 | Plug | Filter Plug (Clean Water System) | FLT PLG |  | 9.86e-08 | h | 8.4
27 | Hose Connector | Piping Non-Service Water System External Leak Small | PIPE OTHER | ELS | 2.53e-10 | h-ft | 8.4
27 | Hose Connector | Piping Non-Service Water System External Leak Large | PIPE OTHER | ELL | 2.53e-11 | h-ft | 18.8
28 | Spool | Piping Non-Service Water System External Leak Small | PIPE OTHER | ELS | 2.53e-10 | h-ft | 8.4
28 | Spool | Piping Non-Service Water System External Leak Large | PIPE OTHER | ELL | 2.53e-11 | h-ft | 18.8
29 | Swivel Joint | Piping Non-Service Water System External Leak Small | PIPE OTHER | ELS | 2.53e-10 | h-ft | 8.4
29 | Swivel Joint | Piping Non-Service Water System External Leak Large | PIPE OTHER | ELL | 2.53e-11 | h-ft | 18.8
30 | Pump Motor | Motor-Driven Pump (Running) Fail to Run | MDP | FTR | 4.54e-06 | h | 3.1
30 | Pump Motor | Motor-Driven Pump (Running) Fail to Start | MDP | FTS | 0.00223 | d | 4.8
31 | Sight Glass | Piping Non-Service Water System External Leak Small | PIPE OTHER | ELS | 2.53e-10 | h-ft | 8.4
31 | Sight Glass | Piping Non-Service Water System External Leak Large | PIPE OTHER | ELL | 2.53e-11 | h-ft | 18.8
32 | Loading Arm | Piping Non-Service Water System External Leak Small | PIPE OTHER | ELS | 2.53e-10 | h-ft | 8.4
32 | Loading Arm | Piping Non-Service Water System External Leak Large | PIPE OTHER | ELL | 2.53e-11 | h-ft | 18.8
33 | Change in Line Size (reducer) | Piping Non-Service Water System External Leak Small | PIPE OTHER | ELS | 2.53e-10 | h-ft | 8.4
33 | Change in Line Size (reducer) | Piping Non-Service Water System External Leak Large | PIPE OTHER | ELL | 2.53e-11 | h-ft | 18.8
34 | Locally Mounted Instrument | Sensor/Transmitter (Flow) Fail to Operate | STF | FTOP | 0.000815 | d | 8.4
35 | Main Panel Mounted Instrument | Sensor/Transmitter (Flow) Fail to Operate | STF | FTOP | 0.000815 | d | 8.4
36 | Instrument Mounted Behind Main Panel | Sensor/Transmitter (Flow) Fail to Operate | STF | FTOP | 0.000815 | d | 8.4
37 | Local Panel Mounted Instrument | Sensor/Transmitter (Flow) Fail to Operate | STF | FTOP | 0.000815 | d | 8.4
38 | Instrument Mounted Behind Local Panel | Sensor/Transmitter (Flow) Fail to Operate | STF | FTOP | 0.000815 | d | 8.4
39 | Instrument with two functions | Sensor/Transmitter (Flow) Fail to Operate | STF | FTOP | 0.000815 | d | 8.4
40 | Indicator Light | Sensor/Transmitter (Flow) Fail to Operate | STF | FTOP | 0.000815 | d | 8.4
41 | Local Pump Controller | Process Logic (Flow) Fail to Operate | PLF | FTOP | 0.000625 | d | 8.4
42 | Interface to Flow Computer Digital Highway | Process Logic (Flow) Fail to Operate | PLF | FTOP | 0.000625 | d | 8.4
43 | Interface to Valve Control I/O | Process Logic (Flow) Fail to Operate | PLF | FTOP | 0.000625 | d | 8.4
44 | Tank Interface Unit | Process Logic (Flow) Fail to Operate | PLF | FTOP | 0.000625 | d | 8.4
45 | Interface to PLC | Process Logic (Flow) Fail to Operate | PLF | FTOP | 0.000625 | d | 8.4
46 | Shared Display Control System Operator Interface | Sensor/Transmitter (Flow) Fail to Operate | STF | FTOP | 0.000815 | d | 8.4
47 | Interlock Logic | Process Logic (Flow) Fail to Operate | PLF | FTOP | 0.000625 | d | 8.4
48 | Remote Reset Electrical Coil | Bistable Fail to Operate | BIS | FTOP | 0.000544 | d | 8.4
49 | Strobe Light | Sensor/Transmitter (Flow) Fail to Operate | STF | FTOP | 0.000815 | d | 8.4
50 | Audible Alarm | Sensor/Transmitter (Flow) Fail to Operate | STF | FTOP | 0.000815 | d | 8.4
51 | Enroute Booster Pump Controller | Process Logic (Flow) Fail to Operate | PLF | FTOP | 0.000625 | d | 8.4
52 | Pipe Line Leak Detection System | Sensor/Transmitter (Flow) Fail to Operate | STF | FTOP | 0.000815 | d | 8.4
53 | Turbine or Propeller Type Flow Meter | Sensor/Transmitter (Flow) Fail to Operate | STF | FTOP | 0.000815 | d | 8.4
54 | Positive Displacement Flow Meter | Sensor/Transmitter (Flow) Fail to Operate | STF | FTOP | 0.000815 | d | 8.4
55 | Area Volume Flow Meter | Sensor/Transmitter (Flow) Fail to Operate | STF | FTOP | 0.000815 | d | 8.4
56 | Accoustic Flow Meter | Sensor/Transmitter (Flow) Fail to Operate | STF | FTOP | 0.000815 | d | 8.4
57 | Totalizer Flow Meter | Sensor/Transmitter (Flow) Fail to Operate | STF | FTOP | 0.000815 | d | 8.4
58 | Flow Meter Flow Conditioner | Sensor/Transmitter (Flow) Fail to Operate | STF | FTOP | 0.000815 | d | 8.4
59 | Thermowell | Sensor/Transmitter (Temperature) Fail to Operate | STT | FTOP | 0.000432 | d | 8.4
60 | Tank | Tank Unpressurized External Leak Small | TNK UNPR | ELS | 3.19e-08 | h | 8.4
60 | Tank | Tank Unpressurized External Leak Large | TNK UNPR | ELL | 2.23e-09 | h | 18.8
61 | Pump | Motor-Driven Pump (Running) Fail to Run | MDP | FTR | 4.54e-06 | h | 3.1
61 | Pump | Motor-Driven Pump (Running) Fail to Start | MDP | FTS | 0.00223 | d | 4.8
62 | Gear Pump | Motor-Driven Pump (Running) Fail to Run | MDP | FTR | 4.54e-06 | h | 3.1
62 | Gear Pump | Motor-Driven Pump (Running) Fail to Start | MDP | FTS | 0.00223 | d | 4.8
63 | Vertical Centrifugal Pump | Motor-Driven Pump (Running) Fail to Run | MDP | FTR | 4.54e-06 | h | 3.1
63 | Vertical Centrifugal Pump | Motor-Driven Pump (Running) Fail to Start | MDP | FTS | 0.00223 | d | 4.8
64 | Sump Pump | Motor-Driven Pump (Running) Fail to Run | MDP | FTR | 4.54e-06 | h | 3.1
64 | Sump Pump | Motor-Driven Pump (Running) Fail to Start | MDP | FTS | 0.00223 | d | 4.8
65 | Primary Processing Piping | Piping Non-Service Water System External Leak Small | PIPE OTHER | ELS | 2.53e-10 | h-ft | 8.4
65 | Primary Processing Piping | Piping Non-Service Water System External Leak Large | PIPE OTHER | ELL | 2.53e-11 | h-ft | 18.8
66 | Secondary Process Piping | Piping Non-Service Water System External Leak Small | PIPE OTHER | ELS | 2.53e-10 | h-ft | 8.4
66 | Secondary Process Piping | Piping Non-Service Water System External Leak Large | PIPE OTHER | ELL | 2.53e-11 | h-ft | 18.8
67 | Utility Process Piping | Piping Non-Service Water System External Leak Small | PIPE OTHER | ELS | 2.53e-10 | h-ft | 8.4
67 | Utility Process Piping | Piping Non-Service Water System External Leak Large | PIPE OTHER | ELL | 2.53e-11 | h-ft | 18.8
68 | Valve PIT Limit | Sensor/Transmitter (Flow) Fail to Operate | STF | FTOP | 0.000815 | d | 8.4
69 | Intrument Line - Electrical | Sensor/Transmitter (Flow) Fail to Operate | STF | FTOP | 0.000815 | d | 8.4
70 | Instrument Line - Pnumatic | Sensor/Transmitter (Flow) Fail to Operate | STF | FTOP | 0.000815 | d | 8.4
71 | Instrument Line - Capillary | Sensor/Transmitter (Flow) Fail to Operate | STF | FTOP | 0.000815 | d | 8.4
72 | Instrument Line - Hydraulic | Sensor/Transmitter (Flow) Fail to Operate | STF | FTOP | 0.000815 | d | 8.4
73 | Instrument Line - Mechanical | Sensor/Transmitter (Flow) Fail to Operate | STF | FTOP | 0.000815 | d | 8.4
74 | Instrument Line - Electronic Data or Software Link | Process Logic (Flow) Fail to Operate | PLF | FTOP | 0.000625 | d | 8.4
75 | Automated Valve | Motor-Operated Valve Fail to Control | MOV | FC | 3e-06 | h | 18.8
75 | Automated Valve | Motor-Operated Valve Fail to Open or Close | MOV | FTO/C | 0.00107 | d | 3.6
75 | Automated Valve | Motor-Operated Valve Spurious Operation | MOV | SO | 4.45e-08 | h | 8.4
75 | Automated Valve | Motor-Operated Valve External Leak Small | MOV | ELS | 1.41e-08 | h | 8.4
75 | Automated Valve | Motor-Operated Valve External Leak Large | MOV | ELL | 9.84e-10 | h | 18.8
75 | Automated Valve | Motor-Operated Valve Internal Leak Small | MOV | ILS | 1.67e-07 | h | 10.2
75 | Automated Valve | Motor-Operated Valve Internal Leak Large | MOV | ILL | 3.34e-09 | h | 18.8
82 | Flow Computer | Process Logic (Flow) Fail to Operate | PLF | FTOP | 0.000625 | d | 8.4
83 | Flow Transmitter | Sensor/Transmitter (Flow) Fail to Operate | STF | FTOP | 0.000815 | d | 8.4
84 | Low Flow Switch | Sensor/Transmitter (Flow) Fail to Operate | STF | FTOP | 0.000815 | d | 8.4
85 | Flow Computer Interface | Process Logic (Flow) Fail to Operate | PLF | FTOP | 0.000625 | d | 8.4
86 | Flow Conditioner | Process Logic (Flow) Fail to Operate | PLF | FTOP | 0.000625 | d | 8.4
87 | Ground Reader | Sensor/Transmitter (Temperature) Fail to Operate | STT | FTOP | 0.000432 | d | 8.4
88 | Ground Saftey System | Sensor/Transmitter (Temperature) Fail to Operate | STT | FTOP | 0.000432 | d | 8.4
89 | Hand Switch (Or pushbutton) | Circuit Breaker Spurious Operation | CBK | SO | 1.71e-07 | h | 2.8
90 | Hand Valve | Manual Valve Fail to Open or Close | XVM | FTO/C | 0.000743 | d | 8.4
90 | Hand Valve | Manual Valve Plug | XVM | PLG | 6.36e-09 | h | 8.4
90 | Hand Valve | Manual Valve External Leak Small | XVM | ELS | 4.46e-08 | h | 8.4
90 | Hand Valve | Manual Valve External Leak Large | XVM | ELL | 3.12e-09 | h | 18.8
90 | Hand Valve | Manual Valve Internal Leak Small | XVM | ILS | 6.67e-08 | h | 8.4
90 | Hand Valve | Manual Valve Internal Leak Large | XVM | ILL | 1.33e-09 | h | 18.8
91 | Time Delay Relay | Relay Fail to Operate | RLY | FTOP | 2.48e-05 | d | 8.4
92 | Level Alarm High-High | Sensor/Transmitter (Level) Fail to Operate | STL | FTOP | 0.000815 | d | 8.4
93 | Level Element | Sensor/Transmitter (Level) Fail to Operate | STL | FTOP | 0.000815 | d | 8.4
94 | Level Element - Bottom Dediment & Water | Sensor/Transmitter (Level) Fail to Operate | STL | FTOP | 0.000815 | d | 8.4
95 | Level Indicator | Sensor/Transmitter (Level) Fail to Operate | STL | FTOP | 0.000815 | d | 8.4
96 | Level Switch High | Sensor/Transmitter (Level) Fail to Operate | STL | FTOP | 0.000815 | d | 8.4
97 | Level Switch High - High | Sensor/Transmitter (Level) Fail to Operate | STL | FTOP | 0.000815 | d | 8.4
98 | Level Switch Low | Sensor/Transmitter (Level) Fail to Operate | STL | FTOP | 0.000815 | d | 8.4
99 | Level Switch Low - Low | Sensor/Transmitter (Level) Fail to Operate | STL | FTOP | 0.000815 | d | 8.4
100 | Level Safety System | Sensor/Transmitter (Level) Fail to Operate | STL | FTOP | 0.000815 | d | 8.4
101 | Level Transmitter | Sensor/Transmitter (Level) Fail to Operate | STL | FTOP | 0.000815 | d | 8.4
102 | Level Communications Intterface | Process Logic (Level) Fail to Operate | PLL | FTOP | 0.000625 | d | 8.4
103 | Motor Operated Valve | Motor-Operated Valve Fail to Control | MOV | FC | 3e-06 | h | 18.8
103 | Motor Operated Valve | Motor-Operated Valve Fail to Open or Close | MOV | FTO/C | 0.00107 | d | 3.6
103 | Motor Operated Valve | Motor-Operated Valve Spurious Operation | MOV | SO | 4.45e-08 | h | 8.4
103 | Motor Operated Valve | Motor-Operated Valve External Leak Small | MOV | ELS | 1.41e-08 | h | 8.4
103 | Motor Operated Valve | Motor-Operated Valve External Leak Large | MOV | ELL | 9.84e-10 | h | 18.8
103 | Motor Operated Valve | Motor-Operated Valve Internal Leak Small | MOV | ILS | 1.67e-07 | h | 10.2
103 | Motor Operated Valve | Motor-Operated Valve Internal Leak Large | MOV | ILL | 3.34e-09 | h | 18.8
111 | Pressure Differntial Alarm, High | Sensor/Transmitter (Pressure) Fail to Operate | STP | FTOP | 8.22e-07 | h | 8.4
112 | Differential Pressure Indicator | Sensor/Transmitter (Pressure) Fail to Operate | STP | FTOP | 8.22e-07 | h | 8.4
113 | Pressure Differential Switch | Sensor/Transmitter (Pressure) Fail to Operate | STP | FTOP | 8.22e-07 | h | 8.4
114 | Presssure Indicator | Sensor/Transmitter (Pressure) Fail to Operate | STP | FTOP | 8.22e-07 | h | 8.4
115 | Pressure Indicating Transmitter | Sensor/Transmitter (Pressure) Fail to Operate | STP | FTOP | 8.22e-07 | h | 8.4
116 | High Pressure Switch | Sensor/Transmitter (Pressure) Fail to Operate | STP | FTOP | 8.22e-07 | h | 8.4
117 | Programmable Logic Controller | Process Logic (Flow) Fail to Operate | PLF | FTOP | 0.000625 | d | 8.4
118 | Pipeline Leak Detection System | Sensor/Transmitter (Pressure) Fail to Operate | STP | FTOP | 8.22e-07 | h | 8.4
119 | Low Pressure Switch | Sensor/Transmitter (Pressure) Fail to Operate | STP | FTOP | 8.22e-07 | h | 8.4
120 | Pressure Transmitter | Sensor/Transmitter (Pressure) Fail to Operate | STP | FTOP | 8.22e-07 | h | 8.4
121 | Remote Intterface Unit | Process Logic (Flow) Fail to Operate | PLF | FTOP | 0.000625 | d | 8.4
122 | Solenoid Operated Valve | Solenoid-Operated Valve Fail to Control | SOV | FC | 3e-06 | h | 18.8
122 | Solenoid Operated Valve | Solenoid-Operated Valve Fail to Open or Close | SOV | FTO/C | 0.000954 | d | 9.1
122 | Solenoid Operated Valve | Solenoid-Operated Valve Spurious Operation | SOV | SO | 9.23e-08 | h | 18.8
122 | Solenoid Operated Valve | Solenoid-Operated Valve External Leak Small | SOV | ELS | 9.33e-09 | h | 8.4
122 | Solenoid Operated Valve | Solenoid-Operated Valve External Leak Large | SOV | ELL | 6.53e-10 | h | 18.8
122 | Solenoid Operated Valve | Solenoid-Operated Valve Internal Leak Small | SOV | ILS | 2.78e-07 | h | 13.7
122 | Solenoid Operated Valve | Solenoid-Operated Valve Internal Leak Large | SOV | ILL | 5.56e-09 | h | 18.8
123 | Strainer | Strainer Plug | STR | PLG | 7.38e-06 | h | 18.8
124 | High Termperature Alarm | Sensor/Transmitter (Temperature) Fail to Operate | STT | FTOP | 0.000432 | d | 8.4
125 | Temperature Element | Sensor/Transmitter (Temperature) Fail to Operate | STT | FTOP | 0.000432 | d | 8.4
126 | Temperature Element - Lower Elevation | Sensor/Transmitter (Temperature) Fail to Operate | STT | FTOP | 0.000432 | d | 8.4
127 | Temperature Element - Upper Elevation | Sensor/Transmitter (Temperature) Fail to Operate | STT | FTOP | 0.000432 | d | 8.4
128 | Temperature Indication | Sensor/Transmitter (Temperature) Fail to Operate | STT | FTOP | 0.000432 | d | 8.4
129 | Temperature Test Well | Sensor/Transmitter (Temperature) Fail to Operate | STT | FTOP | 0.000432 | d | 8.4
130 | High Temperature Switch | Sensor/Transmitter (Temperature) Fail to Operate | STT | FTOP | 0.000432 | d | 8.4
131 | Temperature Transmitter - Lower Elevation | Sensor/Transmitter (Temperature) Fail to Operate | STT | FTOP | 0.000432 | d | 8.4
132 | Temperature Transmitter - Upper Elevation | Sensor/Transmitter (Temperature) Fail to Operate | STT | FTOP | 0.000432 | d | 8.4
133 | Temperature Transmitter | Sensor/Transmitter (Temperature) Fail to Operate | STT | FTOP | 0.000432 | d | 8.4
134 | High Viberation Alarm | Sensor/Transmitter (Temperature) Fail to Operate | STT | FTOP | 0.000432 | d | 8.4
135 | Valve Control Panel | Sensor/Transmitter (Temperature) Fail to Operate | STT | FTOP | 0.000432 | d | 8.4
136 | Vibration Swtich | Sensor/Transmitter (Temperature) Fail to Operate | STT | FTOP | 0.000432 | d | 8.4
137 | Vibration Transmitter | Sensor/Transmitter (Temperature) Fail to Operate | STT | FTOP | 0.000432 | d | 8.4
138 | Miscellaneous Alarm | Sensor/Transmitter (Temperature) Fail to Operate | STT | FTOP | 0.000432 | d | 8.4
139 | Miscellaneous Indication | Sensor/Transmitter (Temperature) Fail to Operate | STT | FTOP | 0.000432 | d | 8.4
140 | Ground Detector | Bistable Fail to Operate | BIS | FTOP | 0.000544 | d | 8.4
141 | Event Controller | Process Logic (Flow) Fail to Operate | PLF | FTOP | 0.000625 | d | 8.4
142 | Position Switch | Sensor/Transmitter (Temperature) Fail to Operate | STT | FTOP | 0.000432 | d | 8.4
143 | Drain Connection | Piping Non-Service Water System External Leak Small | PIPE OTHER | ELS | 2.53e-10 | h-ft | 8.4
143 | Drain Connection | Piping Non-Service Water System External Leak Large | PIPE OTHER | ELL | 2.53e-11 | h-ft | 18.8
144 | Resistance Temperature Detector | Sensor/Transmitter (Temperature) Fail to Operate | STT | FTOP | 0.000432 | d | 8.4
145 | Tank | Tank Unpressurized External Leak Small | TNK UNPR | ELS | 3.19e-08 | h | 8.4
145 | Tank | Tank Unpressurized External Leak Large | TNK UNPR | ELL | 2.23e-09 | h | 18.8
146 | Battery and UPS | Battery (dc) Fail to Operate | BAT | FTOP | 1.86e-06 | h | 10.4
147 | Fans | Fan (Standby) Fail to Run During First Hour of Operation | FAN STBY | FTR≤1H | 0.00191 | h | 14.3
147 | Fans | Fan (Standby) Fail to Run After First Hour of Operation | FAN STBY | FTR>1H | 0.000111 | h | 1.7
147 | Fans | Fan (Standby) Fail to Start | FAN STBY | FTS | 0.00289 | d | 18.6
148 | Diesel Generator | Emergency Diesel Generator (Standby) Fail to Load and Run During First Hour of Operation | EDG STBY | FTR | 0.0029 | d | 3.4
148 | Diesel Generator | Emergency Diesel Generator (Standby) Fail to Run After First Hour of Operation | EDG STBY | FTR>1H | 0.000848 | h | 2.8
148 | Diesel Generator | Emergency Diesel Generator (Standby) Fail to Start | EDG STBY | FTS | 0.00453 | d | 4.1
149 | Fuel Pipe | Piping Non-Service Water System External Leak Small | PIPE OTHER | ELS | 2.53e-10 | h-ft | 8.4
149 | Fuel Pipe | Piping Non-Service Water System External Leak Large | PIPE OTHER | ELL | 2.53e-11 | h-ft | 18.8