3nd Draft Nov 5, 2014

REPORT TO THE TWENTY-EIGHTH LEGISLATURE

STATE OF HAWAII

2015

PURSUANT TO SENATE CONCURRENT RESOLUTION 73

REQUESTING THE DEPARTMENT OF HEALTH

TO CONVENE A TASK FORCE

TO STUDY THE EFFECTS OF THE JANUARY 2014 FUEL TANK LEAK AT

THE RED HILL FUEL STORAGE FACILITY

PREPARED BY:

STATE OF HAWAII

RED HILL FUEL STORAGE FACILITY TASK FORCE

DECEMBER 2014

Introduction

The Red Hill Fuel Storage Facility is the largest field constructed underground storage tank (UST) facility in Hawaii.  It is owned and operated by the United States Navy, is located near Pearl Harbor and was built between 1940 and 1943.

The facility contains twenty (20) cylindrical tanks each able to store up to 12.5 million gallons of fuel and located 100 feet above a major groundwater aquifer that is used as a source of drinking water.  The tanks have a history of fuel releases dating back to 1949 and Navy test reports document the presence of fuel contaminants in the groundwater and fractured rock beneath the facility.  As a field constructed UST, the Red Hill facility is currently exempt from certain existing state and federal UST regulations under Hawaii Administrative Rules (HAR) Chapter 281 and Title 40 Code of Federal Regulations (CFR) Parts 280.

On January 13, 2014, the Navy reported a 15,000 gallon leak of jet fuel at the facility.  This was later updated to 27,000 gallons estimated to have been lost from Tank 5.  In response to the leak and concerns over the potential impact to Oahu’s drinking water aquifer, the environment and its residents, the Hawaii State Legislature on April 24, 2014 adopted Senate Concurrent Resolution (SCR) 73 which requested the Director of Health to convene a Task Force to study the effects of the January 2014 fuel tank leak at the Red Hill facility and submit a report of the Task Force's findings and recommendations, including any proposed legislation, to the Legislature no later than twenty (20) days prior to the convening of the Regular Session of 2015.

Under SCR 73, the Task Force is requested to examine:

- Short-term and long-term effects of the leak at the Red Hill Underground Fuel Storage Facility, including effects relating to the health of residents, safe drinking water, and the environment,

- Response strategies to mitigate the effects of future leaks at the Red Hill Underground Fuel Storage Facility,

- Ways to improve communication between the United States Navy, the State, and the public in the event of future leaks at the Red Hill Underground Fuel Storage Facility; and

- Implications of closing the Red Hill Underground Fuel Storage Facility.

Task Force members include the U.S. Navy, Hawaii Department of Health (DOH), United States Environmental Protection Agency (EPA), one member from the State House of Representatives, one member from the State Senate, Department of Land and Natural Resources, Honolulu Board of Water Supply (BWS) and two members from the community.  Appendix ____ contains a list of all the Task Force participants and any alternates.

Meetings were held on September 3, October 7, and November 6, 2014 to discuss the effects of the January 2014 release, results of on-going Navy investigations on the tank leak, Navy response actions since the leak was discovered and recommendations for improving operations to ensure protection of Hawaii’s drinking water. These included regulatory requirements, facility improvements and improved communication to the public.  Materials from the three meetings are posted online at: http://health.hawaii.gov/shwb/underground-storage-tanks/.

This report contains the Task Force’s findings and recommendations for each of the review topics in accord with SCR 73.

Findings and Recommendations

- Short-Term and Long-Term Effects of the leak at the Red Hill Fuel Storage Facility including effects relating to the health of residents, safe drinking water, and the environment

Findings

Navy studies and test reports show the Red Hill tanks have a history of fuel releases dating back to 1949 and the presence of fuel contaminants in groundwater and fractured rock beneath the tanks.  Soil vapor and groundwater monitoring well data consistently show petroleum detections from 2005 to the present.  The Task Force deems prevention is less expensive than clean up and water treatment of all releases - large and small.

Samples from Red Hill groundwater monitoring well #2 (RHMW02), located in the tunnel near Tank 5 and Tank 6, contain the highest levels of total petroleum hydrocarbons as diesel (TPH-d) at 12 to 50 times above the DOH environmental action levels (EALs) of 100 µg/L (parts per billion) from 2005 to the present.  The latest groundwater sampling event occurred on July 21, 2014 with 1,300 ppb of TPH-d (1.3 ppm).  Based on Navy monitoring well test results submitted to DOH, the range of petroleum chemical contaminants detected and EPA health advisories, DOH Hazard Evaluation & Emergency Response Office Environmental Action Levels (DOH HEER EALs) and EPA safe drinking water Maximum Contaminant Levels (MCLs) are summarized in Table 1.

Table 1
Petroleum Contaminants Detected

Navy Red Hill Groundwater Monitoring Wells 2005 to 2014

(values that exceed DOH/EPA levels in Bold)

| # | Contaminant | DOH EAL drinking water (ppb) | EPA drinking water MCL** (ppb) | EPA health advisory (ppb) | Minimum value reported (ppb) | Maximum value reported (ppb) |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | TPH-d (diesel) | 100 | None | None | <20 | 5,000 |
| 2 | TPH-g (gasoline) | 100 | None | None | 13.2 | 650 |
| 3 | Xylene | 20 | 10,000 | None | 0.37 | 1.1 |
| 4 | Benzene | 5 | 5 | None | 0.14 | 0.92 |
| 5 | Toluene | 40 | 1,000 | None | 0.5 | 2.5 |
| 6 | Acenaphthene | 20 | None | None | 0.02 | 0.86 |
| 7 | Fluorene | 240 | None | None | 0.03 | 0.3 |
| 8 | 1-methylnaphthalene | 4.7 | None | None | 0.02 | 109 |
| 9 | 2-methylnaphthalene | 10 | None | None | 0.007 | 88.5 |
| 10 | Naphthalene | 17 | None | 100 | 0.03 | 180 |
| 11 | Ethyl benzene | 300 | 700 | None | 0.15 | 0.58 |
| 12 | Lead | 15 | 15 | None | 0.14 | 11.9 |
| 13 | Pyrene | 68 | None | None | 0.03 | 0.11 |
| 14 | Chrysene | 1 | None | None | 0.0159 | 0.062 |
| 15 | Phenanthrene | 240 | None | None | 0.02 | 0.14 |
| 16 | Fluoranthene | 130 | None | None | 0.026 | 0.24 |
| 17 | Benzo[k]fluroanthene | 0.4 | None | None | 0.0068 | 0.017 |
| 18 | Benzo[a] anthracene | 0.092 | None | None | 0.077 | 0.047 |
| 19 | Indeno[1,2,3-c,d]pyrene | 0.092 | None | None | 0.0075 | 0.037 |
| 20 | Benzo[a]pyrene | 0.2 | 0.2 | None | 0.0086 | 0.045 |
| 21 | Benzo[g,h,i]perylene | 0.13 | None | None | 0.0057 | 0.034 |
| 22 | 1,2-dibromoethane (EDB) | 0.04 | None | 0.05 | ND*** | ND*** |
| 23 | 1,2-dichloroethane (1,2 DCA) | 0.15 | None | 5 | ND*** | ND*** |

*ppb = parts per billion same as micrograms per liter

** MCL = maximum contaminant level (EPA safe drinking water standard)

***Non-Detectable however, minimum detection limits were higher than DOH HEER EALs

NOTE: Additional constituents have been analyzed but have not shown significant detections

Soil Vapor sampling points were installed by the Navy beneath each of the 18 operational tanks at Red Hill.  Tank 1 & Tank 19 were removed from service in the 1980s and lack soil vapor sampling points.  The Navy has collected and reported monthly soil vapor for volatile organic compounds (VOCs) by photo ionization detector (PID) beneath each tank from 2008 to present.

Soil vapor VOCs spiked to 225,000 ppbv (parts per billion by volume) beneath Tank 5 in the sampling event of January 15, 2014.  The prior event on December 23, 2013 showed 794 ppbv.  The Navy increased SV monitoring to a weekly basis from Feb 2014 to July 2014.  Maximum SV VOCs beneath Tank 5 increased to 450,000 ppbv on May 1, 2014 and have since declined to 208,000 ppbv on September 25, 2014.

Soil vapor sampling beneath the adjacent Tank 6 showed maximum VOCs of 43,600 ppbv on May 21, 2014 and 18,700 ppbv on September 25, 2014.  Similar results were seen in the direction of Tanks 6-10 and sporadic high readings beneath Tanks 2, 3, 4 indicating air pathways thru the fractured basalt surrounding the tanks within the complex.

Monthly data from the Navy’s soil vapor sampling report for Tank 5 is shown in Table 2.  Figure 1 illustrates this information in graphical form (Navy report, Oct 2014).

Table 2
Soil Vapor Results from SV05

Soil Vapor Monitoring Letter Report
Red Hill Bulk Fuel Storage Facility

Diagram 1 - Locations of the seven monitoring wells routinely tested by the Navy in green, and the two new sentinel wells north installed in Sep/Oct 2014 in blue.

Diagram 1 – Navy Red Hill Monitor Well Locations

Diagram 2 shows a conceptual model of the contamination beneath the Red Hill tanks based on monitoring well sampling results and other sources.

Diagram 2 – Conceptual Site Model

Reference: Red Hill Bulk Fuel Storage Facility Final Groundwater Protection Plan, January 2008, Conceptual Site Model, Fig. 1-5, p. 1-15

Recommendations

- Navy must comply with state requirements for investigation of release points within Tank 5 and characterization and delineation of contamination released, including free product removal to “the maximum extent practicable”.  The Navy has not completed these tasks as of October 31, 2014.  Results of these investigations are urgently needed.

- Request Navy to graphically present all water quality data collected at the Facility by monitoring well location and contaminants detected.

- Continue groundwater modeling studies by the Navy and the BWS.  The studies are critical to understanding the rate and direction of groundwater movement in the area to assess potential impacts to neighboring potable water wells.  The studies will also compliment groundwater monitoring well contaminant data collection to assess the overall condition of the aquifer.

- Navy to drill and install additional groundwater monitoring wells north of the facility and additional groundwater monitoring wells south to enable the collection of groundwater data and provide information for the updated area-wide groundwater modeling.  This will increase and improve the scientific understanding of the present and long-term quality and condition of the aquifer beneath the Red Hill tanks and beyond its boundaries. Select sites for additional monitoring wells after sampling results are obtained from the two monitoring wells installed in September and October 2014.  Obtain relative groundwater elevation data in the Halawa/Red Hill/Moanalua area for proper characterization.

- Devise a mechanism in which the Department of Health, Honolulu Board of Water Supply, and U.S. EPA may be reimbursed for site investigation activities needed to initiate (e.g. installation of additional monitoring wells, any increased groundwater and drinking water sampling, and any water treatment to remove contamination) within the area, to ensure that contamination is not migrating from the Red Hill facility into neighboring drinking water pump stations.

- Strengthen Hawaii’s groundwater protection program by increasing surveillance and identification of potentially contaminating activities from other field constructed tanks to protect and mitigate impacts to groundwater aquifers.

- Navy and Department of Health Safe Drinking Water Branch should monitor the drinking water by collecting and testing duplicate samples for the parameters identified in the existing groundwater and drinking water sampling schedules and other identified by the Honolulu Board of Water Supply. The results should be shared with all interested parties to assure all that Quality Assurance/Quality Control procedures were followed.

- Navy should mitigate existing contamination beneath the tanks starting with the area adjacent to Red Hill ground water monitor well #2 to contain and prevent contamination from extending beyond the current location (e.g. active remedial activities like pump and treat).

- Navy should develop a system to continuously monitor the soil vapor probes with alarm set points to alert operator(s) of organic vapors rising above pre-determined concentrations.

- Response strategies to mitigate the effects of future leaks at the Red Hill Underground Fuel Storage Facility

Findings

The Red Hill facility consists of field constructed USTs that are currently deferred from federal and state UST regulations that require other regulated non-field constructed USTs to have secondary containment for tanks and piping, corrosion protection and leak detection.

Navy documents show the Red Hill tanks have a history of fuel releases dating back to 1949.  Recent maintenance cycles performed on tanks within Red Hill utilize a modified American Petroleum Institute (API) 653 procedure for determining integrity of steel plates and welds.    According to the Navy, the goal of tank maintenance is to have at least 0.1 inches of steel plate remaining at the end of a 20 year operational cycle.  The Navy reported up to 600+ deficiencies within Tank 5 during its maintenance cycle that ended December 2013.  Of the 600+ deficiencies identified, an unknown but significant number of these required patch plates and weld repairs.

All current methods of release detection that the Navy implements at the Facility are reactionary. There is no ‘alarm’ until contamination has entered the environment. Secondary containment would capture fuel released from the inner wall and alert Navy operators of releases.  Barring deficiencies in the outer wall, secondary containment would capture the fuel and prevent releases into the environment.

At the October 7, 2014 Task Force meeting, the Navy stated the importance of the Facility and its need to continually maintain the capacity at Red Hill (15 out of 20 tanks in operations) to support its fuel needs. The Navy also stated that secondary containment is “definitely in the future” of the Red Hill facility and estimated a 20 year time frame to conduct feasibility studies and complete installation of secondary containment.

Recommendations

To mitigate the impact of future releases at Red Hill, the Task Force recommends the following:

- Support proposed EPA regulatory changes to cancel the deferral of field constructed USTs from 40 CFR Parts 280 and 281.

- Issue resolution to encourage Navy to install double-walled secondary containment and real time leak detection at Red Hill.

- DOH agrees with the Navy that double-walled secondary containment and real time leak detection should be implemented at Red Hill.

- Amend the state UST regulations to require secondary containment and leak detection for field constructed USTs.

- Improve communications between the United States Navy, the State, and the public in the event of future leaks at the Red Hill Underground Fuel Storage Facility

Findings

The technical information on Red Hill is primarily communicated between the Navy and DOH and EPA.  Copies are not readily available at a central data location nor easily obtained through written requests.  The Task Force finds that access to this information is essential to its understanding and completing the tasks set before it as described in SCR 73, as well as aiding the public’s understanding of the situation at Red Hill and how it may affect them.

The Task Force finds that all Red Hill tank reports and other information cannot and should not be limited to a few agencies on a facility that has been declassified since 1995.  While the Task Force recognizes the need for confidentiality and agency security policies, these areas should not supersede the need to protect the ground water aquifer, the environment and the welfare of our citizens including their right-to-know.

Recommendations

- Create and maintain a public website containing all information from the Task Force, Navy, DOH, BWS, and other agencies (e.g., meeting notices, notes of meetings, reports, data, trend graphs, laboratory analysis, etc.) to provide easier access to information and improve transparency.

- Continue the work of the Red Hill Task Force to insure the long-term management, information access and decision making on issues related to leaks at Red Hill and the protection of Oahu’s ground water aquifer, environment and public health.

- Utilize notification systems to communicate future leaks and incidences at Red Hill or other underground storage tanks located above or in the vicinity of drinking water aquifers. The alert system should be targeted to specific persons for first response action.

- Implications of Closing the Red Hill Underground Fuel Storage Facility

Findings

The Navy indicated at the October 7, 2014 meeting that assessments are underway to explore alternative fuel storage solutions in lieu of either continued full or partial use of the Red Hill Facility.

Recommendations

The Department of Health does not know the implications of shutting down this facility, nor is it for us to describe. Ultimately, the storage of up to 187 million gallons of fuel, 100 feet above a drinking water resource, is inherently dangerous to the environment.

- The operation of this facility should only exist on the condition that the aging facility be upgraded with secondary containment and state-of-the-art leak detection to ensure safe operations and adverse impact to the environment.

- The Navy should have facility-wide implementation of secondary containment by December 31, 2024.

- In the interim, while the Navy studies available technologies, increased protection and monitoring must be applied until secondary containment can be implemented.

- Legislative Recommendations

- The passing of another resolution that would extend the Red Hill Task Force activities

- To pass an increase in the Environmental Response Revolving Fund (ERRF), that receives its funding primarily from a tax of 5 cents, on every barrel of oil imported into the State under the Environmental Response, Energy, and Food Security Tax (“Barrel Tax”), to 15 cents. This will provide the Solid & Hazardous Waste Branch and the Safe Drinking Water Branch additional personnel and resources to support oversight to the Red Hill case over the next ten years.

- Support adoption of revisions to existing DOH UST rules requiring increased protection from Hawaii’s 46 field constructed tanks, of which Red Hill tanks make up 20. All of these tanks are 70 years or older.

Approval of Report to the Legislature by the Red Hill Task Force Members:

Date:

GARY GILL

Deputy Director for Environmental Health

Date:

AARON POENTIS

Program Director, Navy Region Hawaii

Date:

SENATOR MIKE GABBARD

Chair, Energy/Environmental Committee

Date:

REPRESENTATIVE CHRIS LEE

Energy/Environmental Committee

Date:

STEVE LINDER

Manager, UST Program, EPA Region IX

Date:

ERNEST LAU

Program Manager, Honolulu Board of Water Supply

Date:

PATRICK CASEY

Geologist, DLNR, Commission on Water Resource Mgmt.

Date:

STEVEN ONOUE

President, Moanalua Valley Community Association

Date:

DAVID YOMES

Chair, Aliamanu/Salt Lake Neighborhood Board

# Text boxes

Figure 1
Soil Vapor Measurements

SV05