## Headspace, Gauging, Parameters
Red Hill Bulk Fuel Storage Facility Notice of Interest 20210507-0852 (6 May 2021 Event) Notice of Interest 20211120-2330 (20 Nov 2021 Event) Headspace, Fuel Product Gauging, and Parameters
| HDMW2253-03 Headspace and Product Gauging | [7 empty] | HDMW2253-03 Parameter Readings
WEEK | DATE | AMBIENT | TOP-OF-CASING HEADSPACE | GROUNDWATER HEADSPACE | TAPE | DTW (Raw) | PRODUCT? | THICKNESS | TDS | pH | Sp. Cond. | D.O. | Turbidity | TEMP | ORP | SAL
|  | (ppmv) | (ppmv) | (ppmv) | (Serial #) | (ft btoc) | (Yes/No) | (ft) | (ppm) |  | (mS/cm) | (mg/L) | (NTU) | (°C) | (Mv) | (psu)
07/10/2023 | 07/11/2023 | 0.0 | 0.0 | - | N-6 | 208.12 | No | - | 296.16 | 6.20 | 0.46 | 0.41 | 15.00 | 23.60 | -126.3 | 0.22
08/07/2023 | 08/11/2023 | 0.0 | 0.0 | - | N-6 | 208.23 | No | - | 282.24 | 6.43 | 0.43 | 0.39 | 14.87 | 24.03 | -22.1 | 0.21
09/04/2023 | 09/05/2023 | 0.0 | 0.0 | - | N-6 | 208.3 | No | - | 301.50 | 6.36 | 0.46 | 0.39 | 12.07 | 23.58 | -12.6 | 0.23
10/02/2023 | 10/03/2023 | 0.0 | 0.0 | - | N-6 | 208.37 | No | - | 284.18 | 6.43 | 0.44 | 0.42 | 12.35 | 23.76 | 71.7 | 0.21
11/06/2023 | 11/07/2023 | 0.0 | 0.0 | - | N-4 | 208.51 | No | - | 279.25 | 6.51 | 0.43 | 0.41 | 21.41 | 23.65 | 99.2 | 0.21
2023-12-04 | 2023-12-08 | 0.0 | 0.0 | - | N-5 | 208.33 | No | - | 280.55 | 6.47 | 0.43 | 0.68 | 12.61 | 23.28 | 105.6 | 0.21
2024-01-01 | 2024-01-05 | 0.0 | 0.0 | - | N-6 | 208.29 | No | - | 308.97 | 6.48 | 0.48 | 0.48 | 16.09 | 23.10 | 51.5 | 0.23
2024-02-05 | 2024-02-09 | 0.0 | 0.0 | - | N-6 | 208.05 | No | - | 280.41 | 6.39 | 0.43 | 0.59 | 15.54 | 23.19 | 67.7 | 0.21
2024-03-11 | 2024-03-15 | 0.0 | 0.0 | - | N-5 | 208.13 | No | - | 279.52 | 6.44 | 0.43 | 0.54 | 17.98 | 23.06 | 103.6 | 0.21
2024-03-11 | 2024-04-12 | 0.0 | 0.0 | - | N-4 | 208.28 | No | - | 307.32 | 6.44 | 0.47 | 0.36 | 28.88 | 23.24 | 62.8 | 0.23
2024-03-11 | 2024-05-17 | 0.0 | 0.0 | - | N-2 | 207.98 | No | - | 269.95 | 6.40 | 0.42 | 0.46 | 16.60 | 23.33 | 115.6 | 0.20
2024-03-11 | 2024-05-28 | 0.0 | 0.0 | - | N-3 | 207.77 | No | - | 296.89 | 6.45 | 0.46 | 0.42 | 17.59 | 23.67 | 118.3 | 0.22
2024-03-11 | 2024-06-14 | 0.0 | 0.0 | - | N-4 | 207.82 | No | - | 305.42 | 6.43 | 0.47 | 0.34 | 25.35 | 23.30 | 114.2 | 0.23
2024-03-11 | 2024-06-28 | 0.0 | 0.0 | - | N-4 | 207.78 | No | - | 270.58 | 6.43 | 0.42 | 0.29 | 26.63 | 23.64 | 105.2 | 0.20
2024-03-11 | 2024-07-12 | 0.0 | 0.0 | - | N-5 | 207.74 | No | - | 274.11 | 6.50 | 0.42 | 0.46 | 28.22 | 23.51 | 67.1 | 0.20
2024-03-11 | 2024-07-26 | 0.0 | 0.0 | - | N-5 | 207.71 | No | - | 342.69 | 6.44 | 0.53 | 0.40 | 13.70 | 23.38 | 120.0 | 0.26
2024-03-11 | 2024-08-15 | 0.0 | 0.0 | - | N-5 | 207.71 | No | - | 272.56 | 6.45 | 0.42 | 0.43 | 9.65 | 23.43 | 99.1 | 0.20
2024-03-11 | 2024-08-30 | 0.0 | 0.0 | - | N-5 | 207.67 | No | - | 291.16 | 6.46 | 0.45 | 0.29 | 12.36 | 23.62 | 113.9 | 0.22
2024-03-11 | 2024-09-13 | 0.0 | 0.0 | - | 252094 | 207.63 | No | - | 279.44 | 6.47 | 0.43 | 0.39 | 35.43 | 23.68 | 82.4 | 0.21
2024-03-11 | 2024-09-27 | 0.0 | 0.0 | - | N-5 | 207.63 | No | - | 267.90 | 6.64 | 0.41 | 0.46 | 15.00 | 23.52 | 46.9 | 0.20
2024-03-11 | 2024-10-18 | 0.0 | 0.0 | - | N-3 | 207.58 | No | - | 304.58 | 6.43 | 0.47 | 0.29 | 44.11 | 23.83 | 22.5 | 0.23
2024-03-11 | 2024-10-31 | 0.0 | 0.0 | - | N-4 | 207.65 | No | - | 273.32 | 6.47 | 0.42 | 0.49 | 20.83 | 23.41 | -51.3 | 0.20
2024-03-11 | 2024-11-15 | 0.0 | 0.0 | - | N-3 | 207.51 | No | - | 277.44 | 6.52 | 0.43 | 0.49 | 24.20 | 23.47 | -40.5 | 0.21
2024-03-11 | 2024-11-25 | 0.0 | 0.0 | - | N-5 | 207.48 | No | - | 288.95 | 6.39 | 0.44 | 0.35 | 20.39 | 23.21 | -23.1 | 0.22
2024-03-11 | 2024-12-13 | 0.0 | 0.0 | - | N-5 | 207.51 | No | - | 284.68 | 6.36 | 0.44 | 0.46 | 16.38 | 23.27 | 88.1 | 0.21
2024-03-11 | 2024-12-27 | 0.0 | 0.0 | - | N-5 | 207.5 | No | - | 294.93 | 6.30 | 0.45 | 0.46 | 13.45 | 23.03 | 74.7 | 0.22
| NMW24 Headspace and Product Gauging | [7 empty] | NMW24 Parameter Readings
WEEK | DATE | AMBIENT | TOP-OF-CASING HEADSPACE | GROUNDWATER HEADSPACE | TAPE | DTW (Raw) | PRODUCT? | THICKNESS | TDS | pH | Sp. Cond. | D.O. | Turbidity | TEMP | ORP | SAL
|  | (ppmv) | (ppmv) | (ppmv) | (Serial #) | (ft btoc) | (Yes/No) | (ft) | (ppm) |  | (mS/cm) | (mg/L) | (NTU) | (°C) | (Mv) | (psu)
06/05/2023 | 06/07/2023 | 0.0 | 0.0 | - | N-3 | 90.63 | No | - | 436.86 | 6.99 | 0.67 | 5.48 | NC2 | 24.25 | 343.0 | 0.33
07/03/2023 | 07/05/2023 | 0.0 | 0.0 | - | N-6 | 90.85 | No | - | 409.40 | 7.07 | 0.63 | 5.77 | 0.00 | 25.94 | 129.4 | 0.31
07/31/2023 | 08/04/2023 | 0.0 | 0.0 | - | N-5 | 90.9 | No | - | 432.87 | 7.05 | 0.67 | 5.33 | 0.31 | 31.12 | 106.8 | 0.33
09/04/2023 | 09/08/2023 | 0.0 | 0.0 | - | N-4 | 91.07 | No | - | 384.17 | 7.17 | 0.59 | 5.80 | 0.00 | 25.5 | 69.5 | 0.29
10/02/2023 | 10/02/2023 | 0.0 | 0.4 | - | N-5 | 91.06 | No | - | 380.96 | 7.14 | 0.59 | 5.92 | 0.67 | 25.86 | 248.1 | 0.29
11/06/2023 | 11/09/2023 | 0.0 | 0.0 | - | N-3 | 91.17 | No | - | 365.40 | 7.10 | 0.56 | 6.06 | 0.13 | 25.76 | 234.1 | 0.27
2023-12-04 | 2023-12-08 | 0.0 | 0.0 | - | N-6 | 90.97 | No | - | 345.72 | 7.21 | 0.53 | 6.12 | 0.61 | 25.44 | 213.5 | 0.26
2024-01-01 | 2024-01-04 | 0.0 | 0.0 | - | N-3 | 90.93 | No | - | 388.93 | 7.34 | 0.60 | 5.98 | 0.06 | 25.42 | 161.4 | 0.29
2024-02-12 | 2024-02-14 | 0.0 | 0.0 | - | N-4 | 90.78 | No | - | 350.48 | 7.06 | 0.54 | 6.00 | 0.26 | 25.32 | 264.6 | 0.26
2024-03-18 | 2024-03-20 | 0.0 | 0.0 | - | N-4 | 90.85 | No | - | 378.20 | 7.09 | 0.58 | 5.94 | 0.40 | 25.37 | 263.1 | 0.28
2024-03-18 | 2024-04-10 | 0.0 | 0.1 | - | N-5 | 90.84 | No | - | 378.83 | 7.03 | 0.58 | 5.95 | 0.73 | 25.81 | 247.3 | 0.29
2024-03-18 | 2024-05-15 | 0.0 | 0.0 | 0.0 | N-5 | 90.69 | No | - | 437.89 | 7.25 | 0.67 | 5.37 | 0.00 | 25.56 | 296.5 | 0.33
2024-03-18 | 2024-05-29 | 0.0 | 0.0 | 0.0 | N-5 | 90.48 | No | - | 396.03 | 7.04 | 0.61 | 5.73 | 0.02 | 25.81 | 254.8 | 0.30
2024-03-18 | 2024-06-12 | 0.0 | 0.0 | 0.0 | N-5 | 90.54 | No | - | 406.91 | 7.04 | 0.63 | 5.57 | 0.00 | 25.72 | 219.2 | 0.31
2024-03-18 | 2024-06-26 | 0.0 | 0.0 | 0.0 | N-5 | 90.56 | No | - | 415.20 | 7.04 | 0.64 | 5.47 | 0.80 | 25.21 | 267.5 | 0.31
2024-03-18 | 2024-07-10 | 0.0 | 0.0 | 0.0 | N-3 | 90.55 | No | - | 421.60 | 7.12 | 0.65 | 5.41 | 0.00 | 25.90 | 231.8 | 0.32
2024-03-18 | 2024-07-26 | 0.0 | 0.0 | 0.0 | N-3 | 90.52 | No | - | 456.62 | 7.22 | 0.70 | 4.86 | 0.17 | 26.17 | 178.4 | 0.35
2024-03-18 | 2024-08-14 | 0.0 | 0.0 | 0.0 | N-5 | 90.54 | No | - | 482.57 | 7.17 | 0.74 | 5.30 | 0.00 | 26.58 | 313.9 | 0.37
2024-03-18 | 2024-08-28 | 0.0 | 0.0 | 0.0 | N-5 | 90.51 | No | - | 481.57 | 7.14 | 0.74 | 5.31 | 0.02 | 25.69 | 262.2 | 0.37
2024-03-18 | 2024-09-12 | 0.0 | 0.0 | 0.0 | 288404 | 90.46 | No | - | 492.38 | 7.16 | 0.76 | 5.24 | 0.00 | 26.36 | 271.3 | 0.37
2024-03-18 | 2024-09-24 | 0.0 | 0.0 | 0.0 | N-4 | 90.45 | No | - | 459.50 | 7.10 | 0.71 | 5.27 | 0.29 | 26.07 | 228.8 | 0.35
2024-03-18 | 2024-10-15 | 0.0 | 0.0 | 0.0 | N-4 | 90.46 | No | - | 466.47 | 7.00 | 0.72 | 5.43 | 0.34 | 25.93 | 278.4 | 0.35
2024-03-18 | 2024-10-31 | 0.0 | 0.0 | 0.0 | N-4 | 90.4 | No | - | 464.83 | 7.08 | 0.72 | 5.07 | 0.29 | 26.24 | 59.4 | 0.35
2024-03-18 | 2024-11-11 | 0.0 | 0.0 | 0.0 | N-5 | 90.31 | No | - | 468.78 | 6.99 | 0.72 | 5.33 | 0.12 | 26.00 | 137.6 | 0.36
2024-03-18 | 2024-11-22 | 0.0 | 0.0 | 0.0 | N-3 | 90.28 | No | - | 495.80 | 7.03 | 0.76 | 5.22 | 0.36 | 25.45 | 152.4 | 0.38
2024-03-18 | 2024-12-10 | 0.0 | 0.0 | 0.0 | N-3 | 90.31 | No | - | 492.87 | 6.97 | 0.76 | 5.38 | 0.09 | 25.76 | 188.4 | 0.37
2024-03-18 | 2024-12-24 | 0.0 | 0.0 | 0.0 | N-5 | 90.31 | No | - | 460.14 | 6.99 | 0.71 | 5.71 | 0.34 | 25.60 | 337.3 | 0.35
| NMW25 Headspace and Product Gauging | [7 empty] | NMW25 Parameter Readings
WEEK | DATE | AMBIENT | TOP-OF-CASING HEADSPACE | GROUNDWATER HEADSPACE | TAPE | DTW (Raw) | PRODUCT? | THICKNESS | TDS | pH | Sp. Cond. | D.O. | Turbidity | TEMP | ORP | SAL
|  | (ppmv) | (ppmv) | (ppmv) | (Serial #) | (ft btoc) | (Yes/No) | (ft) | (ppm) |  | (mS/cm) | (mg/L) | (NTU) | (°C) | (Mv) | (psu)
07/24/2023 | 07/26/2023 | 0.0 | 0.1 | - | N-5 | 190.64 | No | - | 769.27 | 7.26 | 1.18 | 7.95 | 0.79 | 27.91 | 81.6 | 0.60
07/31/2023 | 08/01/2023 | 0.0 | 0.8 | - | N-6 | 190.69 | No | - | 885.86 | 7.31 | 1.36 | 7.69 | 0.46 | 27.78 | 65.2 | 0.69
09/04/2023 | 09/07/2023 | 0.0 | 0.3 | - | N-6 | 190.84 | No | - | 953.68 | 7.17 | 1.47 | 7.33 | 0.71 | 28.01 | 82.8 | 0.74
10/02/2023 | 10/02/2023 | 0.0 | 0.6 | - | N-5 | 190.89 | No | - | 924.46 | 7.10 | 1.42 | 7.89 | 0.36 | 27.13 | 282.0 | 0.72
11/06/2023 | 11/09/2023 | 0.0 | 1.4 | - | N-6 | 190.99 | No | - | 911.22 | 7.12 | 1.40 | 7.90 | 0.38 | 27.51 | 256.6 | 0.71
2023-12-04 | 2023-12-07 | 0.0 | 0.5 | - | N-3 | 190.85 | No | - | 909.41 | 7.09 | 1.40 | 7.87 | 0.63 | 26.71 | 224.2 | 0.71
2024-01-01 | 2024-01-04 | 0.0 | 0.0 | - | N-3 | 190.73 | No | - | 957.49 | 7.06 | 1.47 | 7.80 | 0.27 | 26.90 | 227.6 | 0.75
2024-02-12 | 2024-02-14 | 0.0 | 0.0 | - | N-4 | 190.66 | No | - | 907.28 | 7.04 | 1.40 | 7.83 | 0.71 | 26.39 | 257.3 | 0.71
2024-03-18 | 2024-03-20 | 0.0 | 0.0 | - | N-4 | 190.72 | No | - | 947.65 | 7.09 | 1.46 | 7.82 | 1.29 | 26.49 | 254.5 | 0.74
2024-03-18 | 2024-04-10 | 0.0 | 0.0 | - | N-5 | 190.71 | No | - | 916.87 | 6.97 | 1.41 | 7.92 | 1.14 | 26.82 | 260.6 | 0.72
2024-03-18 | 2024-05-15 | 0.0 | 0.0 | 0.0 | N-5 | 190.41 | No | - | 957.57 | 7.04 | 1.47 | 7.74 | 0.17 | 26.65 | 312.1 | 0.75
2024-03-18 | 2024-05-29 | 0.0 | 0.0 | 0.0 | N-5 | 190.24 | No | - | 904.63 | 6.99 | 1.39 | 7.96 | 0.24 | 26.87 | 269.6 | 0.71
2024-03-18 | 2024-06-12 | 0.0 | 0.0 | 0.0 | N-5 | 190.33 | No | - | 900.12 | 7.02 | 1.38 | 7.82 | 0.19 | 26.96 | 210.5 | 0.70
2024-03-18 | 2024-06-26 | 0.0 | 0.0 | 0.0 | N-5 | 190.34 | No | - | 914.66 | 6.91 | 1.41 | 7.84 | 0.69 | 27.29 | 277.7 | 0.71
2024-03-18 | 2024-07-10 | 0.0 | 0.0 | 0.0 | N-3 | 190.33 | No | - | 895.24 | 7.02 | 1.38 | 8.17 | 0.09 | 26.93 | 244.5 | 0.70
2024-03-18 | 2024-07-26 | 0.0 | 0.0 | 0.0 | N-3 | 190.25 | No | - | 903.25 | 7.04 | 1.39 | 7.73 | 0.14 | 26.43 | 286.7 | 0.70
2024-03-18 | 2024-08-14 | 0.0 | 0.0 | 0.0 | N-5 | 190.23 | No | - | 981.87 | 7.01 | 1.51 | 7.54 | 0.37 | 28.61 | 333.6 | 0.77
2024-03-18 | 2024-08-28 | 0.0 | 0.0 | 0.0 | N-5 | 190.31 | No | - | 968.42 | 7.02 | 1.49 | 7.64 | 0.33 | 27.16 | 303.6 | 0.76
2024-03-18 | 2024-09-12 | 0.0 | 0.0 | 0.0 | 288404 | 190.12 | No | - | 969.64 | 7.02 | 1.49 | 7.57 | 1.12 | 28.98 | 278.3 | 0.76
2024-03-18 | 2024-09-24 | 0.0 | 0.0 | 0.0 | N-5 | 190.15 | No | - | 966.14 | 6.94 | 1.49 | 7.58 | 0.52 | 27.13 | 330.0 | 0.76
2024-03-18 | 2024-10-15 | 0.0 | 0.0 | 0.0 | N-4 | 190.11 | No | - | 943.88 | 7.00 | 1.45 | 7.60 | 0.60 | 27.12 | 273.8 | 0.74
2024-03-18 | 2024-10-30 | 0.0 | 0.0 | 0.0 | N-4 | 190.2 | No | - | 869.90 | 6.98 | 1.34 | 7.79 | 0.41 | 26.71 | 89.1 | 0.68
2024-03-18 | 2024-11-11 | 0.0 | 0.0 | 0.0 | N-5 | 189.95 | No | - | 927.09 | 7.00 | 1.43 | 7.72 | 0.32 | 26.63 | 138.4 | 0.72
2024-03-18 | 2024-11-26 | 0.0 | 0.0 | 0.0 | N-4 | 190 | No | - | 973.65 | 6.95 | 1.50 | 7.53 | 0.47 | 26.04 | 228.2 | 0.76
2024-03-18 | 2024-12-06 | 0.0 | 0.0 | 0.0 | N-4 | 189.51 | No | - | 919.22 | 6.92 | 1.41 | 7.63 | 0.30 | 26.28 | 130.8 | 0.72
2024-03-18 | 2024-12-24 | 0.0 | 0.0 | 0.0 | N-3 | 189.99 | No | - | 920.60 | 6.96 | 1.42 | 7.93 | 0.48 | 26.73 | 220.4 | 0.72
| NMW26 Headspace and Product Gauging | [7 empty] | NMW26 Parameter Readings
WEEK | DATE | AMBIENT | TOP-OF-CASING HEADSPACE | GROUNDWATER HEADSPACE | TAPE | DTW (Raw) | PRODUCT? | THICKNESS | TDS | pH | Sp. Cond. | D.O. | Turbidity | TEMP | ORP | SAL
|  | (ppmv) | (ppmv) | (ppmv) | (Serial #) | (ft btoc) | (Yes/No) | (ft) | (ppm) |  | (mS/cm) | (mg/L) | (NTU) | (°C) | (Mv) | (psu)
2024-01-29 | 2024-02-02 | 0.0 | 0.0 | - | N-2 | 750.04 | No | - | 257.28 | 7.70 | 0.40 | 0.46 | 8.51 | 27.73 | 198.7 | 0.19
2024-02-12 | 2024-02-12 | 0.0 | 0.0 | - | N-2 | 750.05 | No | - | 238.78 | 7.65 | 0.37 | 0.84 | 1.20 | 25.77 | -8.0 | 0.18
2024-03-18 | 2024-03-23 | 0.0 | 0.0 | - | N-2 | 750.1 | No | - | 221.82 | 7.62 | 0.34 | 0.80 | 0.54 | 24.99 | 74.2 | 0.16
2024-03-18 | 2024-04-09 | 0.0 | 0.0 | - | N-2 | 750.11 | No | - | 216.21 | 7.58 | 0.33 | 0.96 | 7.05 | 25.33 | 245.9 | 0.16
2024-03-18 | 2024-05-13 | 0.0 | 0.0 | 0.0 | N-2 | 750 | No | - | 217.83 | 7.63 | 0.34 | 0.67 | 2.66 | 24.84 | 298.5 | 0.16
2024-03-18 | 2024-05-28 | 0.0 | 0.0 | 0.0 | N-2 | 749.75 | No | - | 227.01 | 7.55 | 0.35 | 0.55 | 0.16 | 24.94 | 92.9 | 0.17
2024-03-18 | 2024-06-10 | 0.0 | 0.0 | 0.0 | N-7 | 749.9 | No | - | 224.02 | 7.99 | 0.34 | 1.25 | 12.62 | 26.32 | 102.2 | 0.17
2024-03-18 | 2024-06-24 | 0.0 | 0.0 | 0.0 | N-7 | 749.95 | No | - | 238.40 | 7.56 | 0.37 | 0.81 | 10.77 | 24.80 | 172.6 | 0.18
2024-03-18 | 2024-07-08 | 0.0 | 0.0 | 0.0 | N-7 | 749.94 | No | - | 225.69 | 7.41 | 0.35 | 0.82 | 0.32 | 25.33 | 29.4 | 0.17
2024-03-18 | 2024-07-24 | 0.0 | 0.0 | 0.0 | N-7 | 749.92 | No | - | 218.17 | 7.61 | 0.34 | 0.71 | 0.00 | 24.99 | 190.4 | 0.16
2024-03-18 | 2024-08-12 | 0.0 | 0.0 | 0.0 | N-7 | 749.93 | No | - | 232.26 | 7.58 | 0.36 | 0.84 | 0.26 | 25.34 | 221.6 | 0.17
2024-03-18 | 2024-08-26 | 0.0 | 0.0 | 0.0 | N-7 | 749.93 | No | - | 211.06 | 7.55 | 0.32 | 0.94 | 0.00 | 24.99 | 186.7 | 0.16
2024-03-18 | 2024-09-11 | 0.0 | 0.0 | 0.0 | 288404 | 749.6 | No | - | 213.51 | 7.61 | 0.33 | 0.68 | 0.07 | 25.18 | 156.3 | 0.16
2024-03-18 | 2024-09-23 | 0.0 | 0.0 | 0.0 | N-7 | 750.64 | No | - | 209.04 | 7.98 | 0.32 | 0.97 | 8.57 | 25.79 | 132.1 | 0.15
2024-03-18 | 2024-10-14 | 0.0 | 0.0 | 0.0 | N-7 | 749.82 | No | - | 217.75 | 8.02 | 0.33 | 0.78 | 0.81 | 25.27 | 110.7 | 0.16
2024-03-18 | 2024-10-28 | 0.0 | 0.0 | 0.0 | N-7 | 749.73 | No | - | 206.19 | 8.07 | 0.32 | 0.71 | 0.42 | 24.59 | -33.4 | 0.15
2024-03-18 | 2024-11-12 | 0.0 | 0.0 | 0.0 | N-7 | 749.7 | No | - | 210.97 | 7.77 | 0.32 | 0.61 | 0.00 | 24.47 | 23.6 | 0.16
2024-03-18 | 2024-11-25 | 0.0 | 0.0 | 0.0 | N-7 | 749.59 | No | - | 284.90 | 7.73 | 0.44 | 0.87 | 0.00 | 24.76 | 158.1 | 0.21
2024-03-18 | 2024-12-09 | 0.0 | 0.0 | 0.0 | N-7 | 749.7 | No | - | 218.37 | 7.77 | 0.34 | 0.98 | 7.97 | 25.21 | 75.4 | 0.16
2024-03-18 | 2024-12-30 | 0.0 | 0.0 | 0.0 | N-7 | 749.69 | No | - | 228.81 | 7.77 | 0.35 | 0.71 | 3.04 | 24.77 | 134.8 | 0.17
| NMW27 Headspace and Product Gauging | [7 empty] | NMW27 Parameter Readings
WEEK | DATE | AMBIENT | TOP-OF-CASING HEADSPACE | GROUNDWATER HEADSPACE | TAPE | DTW (Raw) | PRODUCT? | THICKNESS | TDS | pH | Sp. Cond. | D.O. | Turbidity | TEMP | ORP | SAL
|  | (ppmv) | (ppmv) | (ppmv) | (Serial #) | (ft btoc) | (Yes/No) | (ft) | (ppm) |  | (mS/cm) | (mg/L) | (NTU) | (°C) | (Mv) | (psu)
2024-01-29 | 2024-10-09 | 0.0 | 0.0 | - | N-5 | 112.95 | No | - | 1206.09 | 7.85 | 1.86 | 9.34 | 3.35 | 27.23 | 165.7 | 0.95
2024-01-29 | 2024-10-28 | 0.0 | 0.0 | - | N-7 | 108.01 | No | - | 1175.12 | 8.77 | 1.81 | 6.18 | 1.44 | 27.39 | 30.0 | 0.93
2024-01-29 | 2024-11-15 | 0.0 | 0.0 | - | N-5 | 107.91 | No | - | 1311.83 | 9.07 | 2.02 | 5.72 | 0.00 | 27.40 | 65.2 | 1.04
2024-01-29 | 2024-11-25 | 0.0 | 0.0 | - | N-3 | 107.87 | No | - | 1279.50 | 9.01 | 1.97 | 5.25 | 2.97 | 27.55 | 108.0 | 1.01
2024-01-29 | 2024-12-13 | 0.0 | 0.0 | - | N-3 | 107.97 | No | - | 1231.97 | 8.87 | 1.90 | 4.55 | 6.28 | 27.41 | 180.1 | 0.97
2024-01-29 | 2024-12-24 | 0.0 | 0.0 | - | N-3 | 108 | No | - | 1209.92 | 8.71 | 1.86 | 3.90 | 13.09 | 27.15 | 131.0 | 0.96
| NMW30 Headspace and Product Gauging | [7 empty] | NMW30 Parameter Readings
WEEK | DATE | AMBIENT | TOP-OF-CASING HEADSPACE | GROUNDWATER HEADSPACE | TAPE | DTW (Raw) | PRODUCT? | THICKNESS | TDS | pH | Sp. Cond. | D.O. | Turbidity | TEMP | ORP | SAL
|  | (ppmv) | (ppmv) | (ppmv) | (Serial #) | (ft btoc) | (Yes/No) | (ft) | (ppm) |  | (mS/cm) | (mg/L) | (NTU) | (°C) | (Mv) | (psu)
10/16/2023 | 10/19/2023 | 0.0 | 0.0 | - | N-5 | 291.65 | No | - | 457.81 | 7.51 | 0.70 | 0.30 | 1.42 | 27.40 | -8.5 | 0.35
11/06/2023 | 11/09/2023 | 0.0 | 0.0 | - | N-5 | 291.71 | No | - | 436.77 | 7.50 | 0.70 | 0.20 | 3.09 | 26.54 | -161.4 | 0.33
2023-12-04 | 2023-12-07 | 0.0 | 10.0 | - | N-3 | 291.54 | No | - | 425.62 | 7.47 | 0.65 | 0.29 | 3.59 | 25.66 | -55.9 | 0.32
2024-01-01 | 2024-01-04 | 0.0 | 0.1 | - | N-5 | 291.45 | No | - | 1048.99 | 7.52 | 1.61 | 0.32 | 0.77 | 25.33 | -18.8 | 0.82
2024-02-12 | 2024-02-15 | 0.0 | 0.0 | - | N-6 | 291.35 | No | - | 445.01 | 7.47 | 0.68 | 0.47 | 1.27 | 24.85 | -48.0 | 0.34
2024-03-18 | 2024-03-20 | 0.0 | 0.0 | - | N-2 | 291.43 | No | - | 421.34 | 7.46 | 0.65 | 0.51 | 0.89 | 25.18 | 42.0 | 0.32
2024-03-18 | 2024-04-11 | 0.0 | 0.0 | - | N-6 | 291.35 | No | - | 415.75 | 7.42 | 0.64 | 0.47 | 2.88 | 25.04 | 59.6 | 0.31
2024-03-18 | 2024-05-16 | 0.0 | 0.0 | 0.0 | N-5 | 291 | No | - | 458.60 | 7.49 | 0.71 | 0.54 | 0.28 | 24.85 | 152.1 | 0.35
2024-03-18 | 2024-05-30 | 0.0 | 0.0 | 0.0 | N-2 | 291.45 | No | - | 441.77 | 7.52 | 0.68 | 0.50 | 10.75 | 25.51 | 117.9 | 0.33
2024-03-18 | 2024-06-13 | 0.0 | 0.0 | 0.0 | N-7 | 290.97 | No | - | 403.29 | 7.35 | 0.62 | 0.81 | 0.00 | 25.55 | 100.5 | 0.30
2024-03-18 | 2024-06-27 | 0.0 | 0.0 | 0.0 | N-3 | 290.91 | No | - | 425.67 | 7.44 | 0.65 | 1.46 | 0.19 | 25.52 | 212.9 | 0.32
2024-03-18 | 2024-07-11 | 0.0 | 0.0 | 0.0 | N-7 | 290.92 | No | - | 392.37 | 7.44 | 0.60 | 1.30 | 1.18 | 26.04 | 87.1 | 0.30
2024-03-18 | 2024-07-25 | 0.0 | 0.0 | 0.0 | N-7 | 291.01 | No | - | 386.09 | 7.46 | 0.59 | 2.13 | 0.26 | 25.62 | 171.5 | 0.29
2024-03-18 | 2024-08-15 | 0.0 | 0.0 | 0.0 | N-7 | 290.97 | No | - | 391.63 | 7.43 | 0.60 | 2.63 | 0.03 | 26.14 | 201.2 | 0.30
2024-03-18 | 2024-08-29 | 0.0 | 0.0 | 0.0 | N-7 | 290.93 | No | - | 389.07 | 7.41 | 0.60 | 3.09 | 0.06 | 25.60 | 239.5 | 0.29
2024-03-18 | 2024-09-12 | 0.0 | 0.0 | 0.0 | 288404 | 290.72 | No | - | 415.45 | 7.44 | 0.64 | 3.12 | 2.52 | 25.99 | 239.8 | 0.31
2024-03-18 | 2024-09-26 | 0.0 | 0.0 | 0.0 | N-4 | 290.82 | No | - | 407.77 | 7.40 | 0.63 | 3.65 | 6.94 | 26.03 | 218.9 | 0.31
2024-03-18 | 2024-10-17 | 0.0 | 0.0 | 0.0 | N-7 | 290.91 | No | - | 381.54 | 7.41 | 0.59 | 3.10 | 1.23 | 26.51 | 228.6 | 0.29
2024-03-18 | 2024-10-30 | 0.0 | 0.0 | 0.0 | N-7 | 290.94 | No | - | 413.67 | 7.37 | 0.64 | 3.52 | 0.00 | 25.28 | 110.4 | 0.31
2024-03-18 | 2024-11-14 | 0.0 | 0.0 | 0.0 | N-7 | 290.82 | No | - | 375.89 | 7.43 | 0.58 | 3.73 | 0.04 | 25.44 | 105.6 | 0.28
2024-03-18 | 2024-11-26 | 0.0 | 0.0 | 0.0 | N-7 | 290.78 | No | - | 394.68 | 7.41 | 0.61 | 4.32 | 0.18 | 25.42 | 215.2 | 0.30
2024-03-18 | 2024-12-12 | 0.0 | 0.0 | 0.0 | N-7 | 290.79 | No | - | 468.62 | 7.33 | 0.72 | 4.04 | 0.15 | 25.28 | 153.4 | 0.36
2024-03-18 | 2024-12-26 | 0.0 | 0.0 | 0.0 | N-4 | 290.61 | No | - | 383.88 | 7.42 | 0.59 | 3.89 | 10.79 | 25.30 | 298.8 | 0.29
| NMW32 Headspace and Product Gauging | [7 empty] | NMW32 Parameter Readings
WEEK | DATE | AMBIENT | TOP-OF-CASING HEADSPACE | GROUNDWATER HEADSPACE | TAPE | DTW (Raw) | PRODUCT? | THICKNESS | TDS | pH | Sp. Cond. | D.O. | Turbidity | TEMP | ORP | SAL
|  | (ppmv) | (ppmv) | (ppmv) | (Serial #) | (ft btoc) | (Yes/No) | (ft) | (ppm) |  | (mS/cm) | (mg/L) | (NTU) | (°C) | (Mv) | (psu)
08/28/2023 | 08/29/2023 | 0.0 | 0.0 | - | N-4 | 170.85 | No | - | 725.49 | 8.00 | 1.12 | 5.03 | 9.31 | 28.72 | 36.8 | 0.56
09/11/2023 | 09/13/2023 | 0.0 | 0.0 | - | N-5 | 170.68 | No | - | 735.75 | 7.30 | 1.13 | 5.52 | 1.28 | 27.70 | 81.3 | 0.57
10/02/2023 | 10/03/2023 | 0.0 | 0.0 | - | N-5 | 170.79 | No | - | 709.74 | 7.28 | 1.09 | 5.96 | 0.12 | 26.51 | 199.8 | 0.55
11/06/2023 | 11/10/2023 | 0.0 | 0.0 | - | N-5 | 170.9 | No | - | 787.93 | 7.32 | 1.20 | 6.20 | 0.00 | 26.51 | 282.2 | 0.61
2023-12-04 | 2023-12-08 | 0.1 | 0.0 | - | N-6 | 170.77 | No | - | 692.42 | 7.34 | 1.07 | 6.18 | 0.86 | 26.55 | 248.8 | 0.53
2024-01-01 | 2024-01-04 | 0.0 | 0.0 | - | N-5 | 170.66 | No | - | 1735.77 | 7.29 | 2.67 | 5.93 | 0.01 | 26.06 | 243.7 | 1.40
2024-02-12 | 2024-02-15 | 0.0 | 0.0 | - | N-5 | 170.53 | No | - | 680.21 | 7.27 | 1.05 | 5.65 | 0.00 | 25.35 | 223.4 | 0.52
2024-03-18 | 2024-03-21 | 0.0 | 0.0 | - | N-4 | 170.67 | No | - | 686.11 | 7.29 | 1.06 | 5.95 | 0.98 | 25.81 | 266.1 | 0.53
2024-03-18 | 2024-04-11 | 0.0 | 0.0 | - | N-5 | 170.64 | No | - | 683.24 | 7.19 | 1.05 | 5.99 | 0.44 | 26.20 | 232.6 | 0.53
2024-03-18 | 2024-05-16 | 0.0 | 0.0 | 0.0 | N-5 | 170.24 | No | - | 749.13 | 7.29 | 1.15 | 5.66 | 0.39 | 25.95 | 288.9 | 0.58
2024-03-18 | 2024-05-30 | 0.0 | 0.0 | 0.0 | N-5 | 170.21 | No | - | 699.25 | 7.27 | 1.08 | 4.43 | 0.30 | 26.62 | 217.3 | 0.54
2024-03-18 | 2024-06-13 | 0.0 | 0.0 | 0.0 | N-4 | 170.2 | No | - | 735.95 | 7.32 | 1.13 | 4.90 | 0.41 | 26.73 | 282.3 | 0.57
2024-03-18 | 2024-06-27 | 0.0 | 0.0 | 0.0 | N-3 | 170.17 | No | - | 737.87 | 7.29 | 1.14 | 5.06 | 0.26 | 27.21 | 288.0 | 0.57
2024-03-18 | 2024-07-11 | 0.0 | 0.0 | 0.0 | N-5 | 170.13 | No | - | 697.35 | 7.65 | 1.07 | 4.70 | 1.36 | 26.84 | 194.5 | 0.54
2024-03-18 | 2024-07-25 | 0.0 | 0.0 | 0.0 | N-5 | 170.19 | No | - | 741.19 | 7.26 | 1.14 | 4.85 | 0.41 | 27.15 | 235.9 | 0.57
2024-03-18 | 2024-08-16 | 0.0 | 0.0 | 0.0 | N-3 | 170.32 | No | - | 740.48 | 7.32 | 1.14 | 2.03 | 0.37 | 27.76 | 268.4 | 0.57
2024-03-18 | 2024-08-29 | 0.0 | 0.0 | 0.0 | N-3 | 170.09 | No | - | 697.68 | 7.36 | 1.07 | 5.43 | 0.42 | 27.27 | 278.8 | 0.54
2024-03-18 | 2024-09-11 | 0.0 | 0.0 | 0.0 | 288404 | 170.17 | No | - | 704.62 | 7.28 | 1.08 | 3.80 | 0.22 | 26.97 | 190.4 | 0.54
2024-03-18 | 2024-09-26 | 0.0 | 0.0 | 0.0 | N-4 | 170.06 | No | - | 738.12 | 7.29 | 1.14 | 5.30 | 0.19 | 27.26 | 240.1 | 0.57
2024-03-18 | 2024-10-17 | 0.0 | 0.0 | 0.0 | N-4 | 170.17 | No | - | 725.42 | 7.29 | 1.12 | 4.53 | 0.77 | 26.92 | 162.8 | 0.56
2024-03-18 | 2024-10-29 | 0.0 | 0.0 | 0.0 | N-3 | 170.11 | No | - | 681.49 | 7.28 | 1.05 | 2.89 | 0.78 | 26.27 | 138.4 | 0.52
2024-03-18 | 2024-11-13 | 0.0 | 0.0 | 0.0 | N-4 | 170.03 | No | - | 683.76 | 7.36 | 1.05 | 3.25 | 0.07 | 25.98 | 103.7 | 0.53
2024-03-18 | 2024-11-25 | 0.0 | 0.0 | 0.0 | N-3 | 169.78 | No | - | 744.40 | 7.37 | 1.15 | 4.87 | 0.87 | 26.44 | 170.3 | 0.58
2024-03-18 | 2024-12-11 | 0.0 | 0.0 | 0.0 | N-5 | 169.88 | No | - | 700.87 | 7.21 | 1.08 | 5.24 | 0.20 | 25.84 | 163.5 | 0.54
2024-03-18 | 2024-12-24 | 0.0 | 0.0 | 0.0 | N-4 | 170.02 | No | - | 692.91 | 7.13 | 1.07 | 3.40 | 0.26 | 26.15 | 194.2 | 0.53
| NMW33 Headspace and Product Gauging | [7 empty] | NMW33 Parameter Readings
WEEK | DATE | AMBIENT | TOP-OF-CASING HEADSPACE | GROUNDWATER HEADSPACE | TAPE | DTW (Raw) | PRODUCT? | THICKNESS | TDS | pH | Sp. Cond. | D.O. | Turbidity | TEMP | ORP | SAL
|  | (ppmv) | (ppmv) | (ppmv) | (Serial #) | (ft btoc) | (Yes/No) | (ft) | (ppm) |  | (mS/cm) | (mg/L) | (NTU) | (°C) | (Mv) | (psu)
10/02/2023 | 10/03/2023 | 0.0 | 0.0 | - | N-5 | 118.92 | No | - | 924.43 | 7.57 | 1.42 | 7.44 | 0.28 | 27.83 | 210.5 | 0.72
11/06/2023 | 11/10/2023 | 0.0 | 0.0 | - | N-5 | 117.32 | No | - | 1040.24 | 7.51 | 1.60 | 7.30 | 0.00 | 26.77 | 257.6 | 0.82
2023-12-04 | 2023-12-08 | 0.0 | 0.0 | - | N-5 | 117.41 | No | - | 930.00 | 7.66 | 1.43 | 6.78 | 1.25 | 26.16 | 241.3 | 0.73
2024-01-01 | 2024-01-05 | 0.0 | 0.1 | - | N-5 | 117.57 | No | - | 943.84 | 7.62 | 1.45 | 6.67 | 0.44 | 25.68 | 252.9 | 0.74
2024-02-12 | 2024-02-15 | 0.0 | 0.0 | - | N-5 | 117.69 | No | - | 903.23 | 7.63 | 1.39 | 6.60 | 0.08 | 25.22 | 237.3 | 0.70
2024-03-18 | 2024-03-21 | 0.0 | 0.0 | - | N-4 | 117.84 | No | - | 917.24 | 7.61 | 1.41 | 6.57 | 0.81 | 25.68 | 266.6 | 0.72
2024-03-18 | 2024-04-11 | 0.0 | 0.0 | - | N-5 | 117.8 | No | - | 914.70 | 7.46 | 1.41 | 6.60 | 0.60 | 25.72 | 230.8 | 0.71
2024-03-18 | 2024-05-16 | 0.0 | 0.0 | 0.0 | N-6 | 117.88 | No | - | 896.60 | 7.60 | 1.38 | 6.58 | 0.02 | 24.93 | 272.6 | 0.70
2024-03-18 | 2024-05-30 | 0.0 | 0.0 | 0.0 | N-5 | 117.79 | No | - | 920.06 | 7.55 | 1.42 | 6.68 | 4.48 | 26.53 | 238.5 | 0.72
2024-03-18 | 2024-06-13 | 0.0 | 0.0 | 0.0 | N-4 | 117.74 | No | - | 964.68 | 7.62 | 1.48 | 6.46 | 1.40 | 25.67 | 269.4 | 0.75
2024-03-18 | 2024-06-25 | 0.0 | 0.0 | 0.0 | N-3 | 117.59 | No | - | 905.73 | 7.68 | 1.39 | 6.38 | 0.35 | 26.57 | 242.5 | 0.71
2024-03-18 | 2024-07-11 | 0.0 | 0.0 | 0.0 | N-5 | 117.57 | No | - | 918.00 | 7.63 | 1.41 | 6.72 | 0.60 | 25.87 | 223.0 | 0.72
2024-03-18 | 2024-07-25 | 0.0 | 0.0 | 0.0 | N-5 | 117.58 | No | - | 974.93 | 7.60 | 1.50 | 6.56 | 0.55 | 26.47 | 250.7 | 0.76
2024-03-18 | 2024-08-16 | 0.0 | 0.0 | 0.0 | N-3 | 117.57 | No | - | 851.50 | 7.62 | 1.31 | 6.58 | 0.00 | 26.09 | 297.3 | 0.66
2024-03-18 | 2024-08-29 | 0.0 | 0.0 | 0.0 | N-3 | 117.62 | No | - | 930.49 | 7.60 | 1.43 | 6.75 | 1.85 | 26.55 | 278.8 | 0.73
2024-03-18 | 2024-09-12 | 0.0 | 0.0 | 0.0 | 252094 | 117.67 | No | - | 946.90 | 7.62 | 1.46 | 6.52 | 0.37 | 26.31 | 180.6 | 0.74
2024-03-18 | 2024-09-25 | 0.0 | 0.0 | 0.0 | N-7 | 117.7 | No | - | 940.96 | 7.57 | 1.45 | 6.80 | 0.17 | 26.73 | 232.0 | 0.73
2024-03-18 | 2024-10-17 | 0.0 | 0.0 | 0.0 | N-4 | 117.77 | No | - | 971.93 | 7.62 | 1.50 | 6.57 | 0.10 | 26.20 | 173.1 | 0.76
2024-03-18 | 2024-10-29 | 0.0 | 0.0 | 0.0 | N-3 | 117.67 | No | - | 944.21 | 7.62 | 1.45 | 6.38 | 0.72 | 26.05 | 176.3 | 0.74
2024-03-18 | 2024-11-13 | 0.0 | 0.0 | 0.0 | N-4 | 117.87 | No | - | 925.56 | 7.67 | 1.42 | 6.49 | 0.09 | 25.74 | 106.8 | 0.72
2024-03-18 | 2024-11-25 | 0.0 | 0.0 | 0.0 | N-3 | 117.85 | No | - | 987.58 | 7.66 | 1.52 | 6.62 | 0.50 | 25.45 | 183.5 | 0.77
2024-03-18 | 2024-12-11 | 0.0 | 0.0 | 0.0 | N-5 | 117.85 | No | - | 932.52 | 7.56 | 1.43 | 6.56 | 0.30 | 25.50 | 163.6 | 0.73
2024-03-18 | 2024-12-30 | 0.0 | 0.0 | 0.0 | N-7 | 117.69 | No | - | 990.86 | 7.54 | 1.52 | 6.58 | 0.24 | 25.90 | 247.6 | 0.78
| NMW34 Headspace and Product Gauging | [7 empty] | NMW34 Parameter Readings
WEEK | DATE | AMBIENT | TOP-OF-CASING HEADSPACE | GROUNDWATER HEADSPACE | TAPE | DTW (Raw) | PRODUCT? | THICKNESS | TDS | pH | Sp. Cond. | D.O. | Turbidity | TEMP | ORP | SAL
|  | (ppmv) | (ppmv) | (ppmv) | (Serial #) | (ft btoc) | (Yes/No) | (ft) | (ppm) |  | (mS/cm) | (mg/L) | (NTU) | (°C) | (Mv) | (psu)
2024-03-18 | 2024-03-19 | 0.0 | 0.0 | - | N-5 | 65.1 | No | - | 489.57 | 6.80 | 0.75 | 5.76 | 0.58 | 25.62 | 292.1 | 0.37
2024-03-18 | 2024-04-10 | 0.0 | 0.0 | - | N-4 | 66.22 | No | - | 451.05 | 6.66 | 0.69 | 5.56 | 0.41 | 25.37 | 290.8 | 0.34
2024-03-18 | 2024-05-14 | 0.3 | 0.3 | 0.0 | N-6 | 65.08 | No | - | 465.79 | 6.74 | 0.72 | 5.35 | 0.03 | 25.85 | 307.0 | 0.35
2024-03-18 | 2024-05-28 | 0.0 | 0.0 | 0.0 | N-2 | 64.8 | No | - | 455.84 | 6.64 | 0.70 | 5.38 | 0.13 | 26.08 | 273.5 | 0.35
2024-03-18 | 2024-06-11 | 0.0 | 0.0 | 0.0 | N-5 | 64.85 | No | - | 485.45 | 6.68 | 0.75 | 5.30 | 1.39 | 25.74 | 308.1 | 0.37
2024-03-18 | 2024-06-25 | 0.0 | 0.0 | 0.0 | N-3 | 64.88 | No | - | 417.39 | 6.65 | 0.64 | 5.27 | 0.02 | 25.78 | 277.2 | 0.32
2024-03-18 | 2024-07-09 | 0.4 | 0.0 | 0.0 | N-3 | 64.87 | No | - | 472.00 | 6.41 | 0.73 | 5.79 | 0.50 | 25.92 | 190.1 | 0.36
2024-03-18 | 2024-07-23 | 0.0 | 0.0 | 0.0 | N-5 | 64.88 | No | - | 467.01 | 6.70 | 0.72 | 5.50 | 0.00 | 25.99 | 276.2 | 0.35
2024-03-18 | 2024-08-13 | 0.0 | 0.0 | 0.0 | N-3 | 64.87 | No | - | 431.82 | 6.70 | 0.66 | 5.33 | 0.49 | 25.81 | 224.2 | 0.33
2024-03-18 | 2024-08-27 | 0.0 | 0.0 | 0.0 | N-4 | 64.88 | No | - | 458.91 | 6.64 | 0.71 | 5.39 | 0.00 | 25.60 | 328.3 | 0.35
2024-03-18 | 2024-09-12 | 0.0 | 0.0 | 0.0 | 252094 | 64.76 | No | - | 421.82 | 6.67 | 0.65 | 5.25 | 0.44 | 26.52 | 217.2 | 0.32
2024-03-18 | 2024-09-23 | 0.0 | 0.0 | 0.0 | N-7 | 64.73 | No | - | 395.63 | 6.73 | 0.61 | 5.20 | 0.30 | 25.88 | 222.7 | 0.30
2024-03-18 | 2024-10-17 | 0.0 | 0.0 | 0.0 | N-4 | 64.76 | No | - | 426.38 | 6.63 | 0.66 | 5.20 | 0.64 | 26.56 | 187.7 | 0.32
2024-03-18 | 2024-10-29 | 0.0 | 0.0 | 0.0 | N-3 | 64.73 | No | - | 393.49 | 6.63 | 0.61 | 4.79 | 0.52 | 25.83 | 222.7 | 0.30
2024-03-18 | 2024-11-15 | 0.0 | 0.0 | 0.0 | N-5 | 64.63 | No | - | 439.87 | 6.62 | 0.68 | 5.24 | 0.00 | 25.70 | 184.7 | 0.33
2024-03-18 | 2024-11-25 | 0.0 | 0.0 | 0.0 | N-5 | 64.61 | No | - | 517.29 | 6.72 | 0.80 | 5.46 | 0.00 | 25.83 | 269.3 | 0.39
2024-03-18 | 2024-12-13 | 0.0 | 0.0 | 0.0 | N-3 | 64.63 | No | - | 391.18 | 6.63 | 0.60 | 5.38 | 0.07 | 25.56 | 312.9 | 0.29
2024-03-18 | 2024-12-24 | 0.0 | 0.0 | 0.0 | N-5 | 64.63 | No | - | 387.96 | 6.67 | 0.60 | 5.41 | 0.42 | 25.74 | 353.8 | 0.29
| OWDFMW03A Headspace and Product Gauging | [7 empty] | OWDFMW03A Parameter Readings
WEEK | DATE | AMBIENT | TOP-OF-CASING HEADSPACE | GROUNDWATER HEADSPACE | TAPE | DTW (Raw) | PRODUCT? | THICKNESS | TDS | pH | Sp. Cond. | D.O. | Turbidity | TEMP | ORP | SAL
|  | (ppmv) | (ppmv) | (ppmv) | (Serial #) | (ft btoc) | (Yes/No) | (ft) | (ppm) |  | (mS/cm) | (mg/L) | (NTU) | (°C) | (Mv) | (psu)
2024-03-18 | 2024-05-15 | 0.0 | 0.4 | - | N-6 | 100.69 | No | - | 241.20 | 7.99 | 0.37 | 2.00 | 1.35 | 25.53 | 182.0 | 0.18
2024-03-18 | 2024-05-31 | 0.0 | 0.0 | - | N-5 | 100.56 | No | - | 264.91 | 8.20 | 0.41 | 2.08 | 0.54 | 25.88 | 217.9 | 0.20
2024-03-18 | 2024-06-14 | 0.0 | 0.0 | - | N-3 | 100.5 | No | - | 241.74 | 7.95 | 0.37 | 1.30 | 6.34 | 25.94 | 131.1 | 0.18
2024-03-18 | 2024-06-26 | 0.0 | 0.0 | - | N-3 | 100.7 | No | - | 280.69 | 8.23 | 0.43 | 0.78 | 0.23 | 25.82 | 165.9 | 0.21
2024-03-18 | 2024-07-10 | 0.0 | 0.0 | - | N-4 | 100.63 | No | - | 250.37 | 8.30 | 0.39 | 1.37 | 0.31 | 26.04 | 191.7 | 0.19
2024-03-18 | 2024-07-24 | 0.0 | 0.0 | - | N-5 | 100.72 | No | - | 277.63 | 8.24 | 0.43 | 1.51 | 2.01 | 25.94 | 172.8 | 0.21
2024-03-18 | 2024-08-28 | 0.0 | 0.0 | - | N-3 | 100.66 | No | - | 255.26 | 8.24 | 0.39 | 1.88 | 39.53 | 25.84 | 151.0 | 0.19
2024-03-18 | 2024-09-09 | 0.0 | 0.0 | - | N-3 | 100.35 | No | - | 243.44 | 8.33 | 0.37 | 2.25 | 3.95 | 26.43 | 153.5 | 0.18
2024-03-18 | 2024-09-24 | 0.0 | 0.0 | - | N-4 | 100.5 | No | - | 244.61 | 7.93 | 0.38 | 2.26 | 2.21 | 27.06 | 158.7 | 0.18
2024-03-18 | 2024-10-16 | 0.0 | 0.0 | - | N-4 | 100.52 | No | - | 245.14 | 8.04 | 0.38 | 1.21 | 2.85 | 25.99 | 167.4 | 0.18
2024-03-18 | 2024-10-31 | 0.0 | 0.0 | - | N-3 | 100.32 | No | - | 268.12 | 7.82 | 0.41 | 1.25 | 3.43 | 26.40 | 64.1 | 0.20
2024-03-18 | 2024-11-13 | 0.0 | 0.0 | - | N-3 | 100.37 | No | - | 259.94 | 7.90 | 0.40 | 1.28 | 0.70 | 25.62 | 43.5 | 0.19
2024-03-18 | 2024-11-25 | 0.0 | 0.0 | - | N-5 | 100.18 | No | - | 249.55 | 7.91 | 0.38 | 1.21 | 0.55 | 26.22 | 43.0 | 0.19
2024-03-18 | 2024-12-11 | 0.0 | 0.0 | - | N-3 | 100.18 | No | - | 246.35 | 8.14 | 0.38 | 1.10 | 1.35 | 25.55 | 172.9 | 0.18
2024-03-18 | 2024-12-30 | 0.0 | 0.0 | - | N-3 | 100.18 | No | - | 250.19 | 8.08 | 0.38 | 1.25 | 0.69 | 25.50 | 167.7 | 0.19
| OWDFMW08A Headspace and Product Gauging | [7 empty] | OWDFMW08A Parameter Readings
WEEK | DATE | AMBIENT | TOP-OF-CASING HEADSPACE | GROUNDWATER HEADSPACE | TAPE | DTW (Raw) | PRODUCT? | THICKNESS | TDS | pH | Sp. Cond. | D.O. | Turbidity | TEMP | ORP | SAL
|  | (ppmv) | (ppmv) | (ppmv) | (Serial #) | (ft btoc) | (Yes/No) | (ft) | (ppm) |  | (mS/cm) | (mg/L) | (NTU) | (°C) | (Mv) | (psu)
2024-03-18 | 2024-05-15 | 0.0 | 0.2 | - | N-6 | 115.8 | No | - | 674.74 | 7.04 | 1.04 | 4.68 | 0.88 | 25.47 | 144.3 | 0.52
2024-03-18 | 2024-05-31 | 0.0 | 0.0 | - | N-5 | 115.71 | No | - | 715.63 | 7.09 | 1.10 | 4.99 | 7.78 | 25.47 | 273.0 | 0.55
2024-03-18 | 2024-06-12 | 0.0 | 0.0 | - | N-4 | 115.78 | No | - | 722.36 | 7.03 | 1.11 | 4.91 | 1.52 | 25.45 | 285.2 | 0.56
2024-03-18 | 2024-06-26 | 0.0 | 0.0 | - | N-3 | 115.79 | No | - | 744.06 | 7.04 | 1.14 | 5.02 | 0.46 | 25.83 | 291.6 | 0.57
2024-03-18 | 2024-07-10 | 0.0 | 0.0 | - | N-4 | 115.72 | No | - | 673.15 | 7.08 | 1.04 | 4.91 | 0.93 | 25.75 | 115.8 | 0.52
2024-03-18 | 2024-07-24 | 0.0 | 0.0 | - | N-5 | 115.79 | No | - | 729.84 | 7.05 | 1.12 | 5.00 | 0.70 | 25.87 | 244.4 | 0.56
2024-03-18 | 2024-08-28 | 0.0 | 0.0 | - | N-3 | 115.75 | No | - | 674.13 | 7.06 | 1.04 | 5.58 | 2.08 | 25.54 | 187.0 | 0.52
2024-03-18 | 2024-09-11 | 0.0 | 0.0 | - | 252094 | 115.64 | No | - | 719.69 | 7.02 | 1.11 | 5.38 | 0.00 | 26.07 | 290.0 | 0.56
2024-03-18 | 2024-09-24 | 0.0 | 0.0 | - | N-7 | 115.58 | No | - | 714.41 | 7.00 | 1.10 | 5.27 | 0.00 | 25.99 | 287.9 | 0.55
2024-03-18 | 2024-10-16 | 0.0 | 0.0 | - | N-4 | 115.65 | No | - | 652.55 | 7.20 | 1.00 | 5.01 | 0.25 | 25.84 | 183.9 | 0.50
2024-03-18 | 2024-10-31 | 0.0 | 0.0 | - | N-3 | 115.42 | No | - | 716.46 | 6.97 | 1.10 | 5.11 | 0.00 | 25.81 | 145.4 | 0.55
2024-03-18 | 2024-11-13 | 0.0 | 0.0 | - | N-3 | 115.5 | No | - | 708.71 | 7.06 | 1.09 | 5.13 | 0.41 | 25.09 | 139.2 | 0.55
2024-03-18 | 2024-11-25 | 0.0 | 0.0 | - | N-5 | 115.3 | No | - | 695.21 | 7.08 | 1.07 | 4.77 | 0.38 | 25.79 | 119.2 | 0.54
2024-03-18 | 2024-12-11 | 0.0 | 0.0 | - | N-3 | 115.28 | No | - | 690.79 | 7.10 | 1.06 | 5.02 | 0.16 | 25.38 | 214.5 | 0.53
2024-03-18 | 2024-12-30 | 0.0 | 0.0 | - | N-3 | 115.3 | No | - | 701.80 | 7.05 | 1.08 | 4.84 | 0.31 | 25.46 | 226.9 | 0.54
| RHMW01R Headspace and Product Gauging | [7 empty] | RHMW01R Parameter Readings
WEEK | DATE | AMBIENT | TOP-OF-CASING HEADSPACE | GROUNDWATER HEADSPACE | TAPE | DTW (Raw) | PRODUCT? | THICKNESS | TDS | pH | Sp. Cond. | D.O. | Turbidity | TEMP | ORP | SAL
|  | (ppmv) | (ppmv) | (ppmv) | (Serial #) | (ft btoc) | (Yes/No) | (ft) | (ppm) |  | (mS/cm) | (mg/L) | (NTU) | (°C) | (Mv) | (psu)
06/12/2023 | 06/15/2023 | 0.0 | 0.0 | - | N-3 | 83.72 | No | - | 205.35 | 7.12 | 0.32 | 0.59 | 0.00 | 23.35 | -275.4 | 0.15
07/03/2023 | 07/07/2023 | 0.0 | 0.0 | - | N-3 | 83.5 | No | - | 206.66 | 7.08 | 0.32 | 0.62 | 0.00 | 23.52 | -103.9 | 0.15
07/31/2023 | 08/01/2023 | 0.0 | 0.1 | - | N-4 | 84.05 | No | - | 200.40 | 6.98 | 0.31 | 0.58 | 0.00 | 26.73 | -206.0 | 0.15
09/04/2023 | 09/05/2023 | 0.0 | 0.0 | - | N-4 | 84.16 | No | - | 209.84 | 7.18 | 0.32 | 0.39 | 0.00 | 23.49 | -229.0 | 0.16
10/02/2023 | 10/04/2023 | 0.0 | 0.0 | - | N-4 | 83.28 | No | - | 204.25 | 6.98 | 0.31 | 0.49 | 0.00 | 23.42 | -56.3 | 0.15
10/16/2023 | 10/17/2023 | 0.0 | 0.3 | - | N-4 | 84.34 | No | - | 218.71 | 7.11 | 0.34 | 0.49 | 0.24 | 23.40 | -82.4 | 0.16
10/23/2023 | 10/24/2023 | 0.0 | 0.1 | - | N-4 | 84.35 | No | - | 211.41 | 7.13 | 0.33 | 0.47 | 0.17 | 23.29 | -68.4 | 0.16
10/30/2023 | 10/31/2023 | 0.0 | 0.0 | - | N-6 | 84.31 | No | - | 217.56 | 7.09 | 0.33 | 0.46 | 0.00 | 23.29 | -47.1 | 0.16
11/06/2023 | 11/06/2023 | 0.0 | 0.0 | - | N-4 | 84.39 | No | - | 209.60 | 7.17 | 0.30 | 0.50 | 0.17 | 23.50 | -82.0 | 0.16
11/06/2023 | 11/07/2023 | 0.0 | 0.0 | - | N-5 | 84.34 | No | - | 212.67 | 7.09 | 0.30 | 0.40 | 0.13 | 23.55 | -55.6 | 0.16
2023-11-13 | 2023-11-13 | 0.0 | 0.3 | - | N-3 | 84.34 | No | - | 209.45 | 7.17 | 0.32 | 0.54 | 0.00 | 23.54 | -106.3 | 0.16
2023-11-20 | 2023-11-24 | 0.0 | 0.0 | - | N-5 | 84.31 | No | - | 203.22 | 7.07 | 0.31 | 0.48 | 0.21 | 23.37 | -88.2 | 0.15
2023-11-27 | 2023-12-01 | 0.0 | 0.0 | - | N-4 | 84.31 | No | - | 211.05 | 7.11 | 0.32 | 0.53 | 0.01 | 23.34 | -62.7 | 0.16
2023-12-04 | 2023-12-08 | 0.0 | 0.0 | - | N-4 | 84.21 | No | - | 204.48 | 7.02 | 0.31 | 0.45 | 0.00 | 23.35 | -43.4 | 0.15
2023-12-11 | 2023-12-15 | 0.0 | 0.0 | - | N-3 | 84.19 | No | - | 192.94 | 7.06 | 0.30 | 0.48 | 0.83 | 23.31 | -50.8 | 0.14
2023-12-18 | 2023-12-19 | 0.0 | 0.0 | - | N-5 | 84.19 | No | - | 182.55 | 7.07 | 0.28 | 0.48 | 0.00 | 23.37 | -32.4 | 0.13
2023-12-25 | 2023-12-26 | 0.0 | 0.0 | - | N-5 | 84.12 | No | - | 193.13 | 7.10 | 0.30 | 0.49 | 0.04 | 23.46 | -38.7 | 0.14
2024-01-01 | 2024-01-05 | 0.0 | 0.1 | - | N-4 | 84.15 | No | - | 193.38 | 6.97 | 0.30 | 0.49 | 0.18 | 23.41 | -44.4 | 0.14
2024-01-08 | 2024-01-12 | 0.0 | 0.0 | - | N-3 | 84.08 | No | - | 195.64 | 7.03 | 0.30 | 0.48 | 0.33 | 23.30 | -22.1 | 0.14
2024-01-15 | 2024-01-19 | 0.2 | 0.9 | - | N-4 | 84.07 | No | - | 193.08 | 6.99 | 0.30 | 0.49 | 1.30 | 23.45 | -24.7 | 0.14
2024-02-12 | 2024-02-16 | 0.0 | 0.0 | - | N-5 | 83.99 | No | - | 189.75 | 6.93 | 0.29 | 0.73 | 0.44 | 23.41 | -20.6 | 0.14
2024-03-11 | 2024-03-13 | 0.0 | 0.0 | - | N-5 | 83.98 | No | - | 190.81 | 6.86 | 0.29 | 0.17 | 0.08 | 23.51 | -52.4 | 0.14
2024-03-11 | 2024-04-04 | 0.0 | 0.0 | - | N-5 | 84.06 | No | - | 185.36 | 6.91 | 0.29 | 0.13 | 0.11 | 23.41 | -20.6 | 0.14
2024-03-11 | 2024-05-09 | 0.0 | 0.3 | 0.0 | N-4 | 83.79 | No | - | 189.15 | 6.96 | 0.29 | 0.23 | 0.19 | 23.54 | -45.1 | 0.14
2024-03-11 | 2024-05-23 | 0.0 | 0.0 | 0.0 | N-5 | 83.61 | No | - | 212.30 | 7.01 | 0.33 | 0.15 | 0.00 | 23.48 | 10.8 | 0.16
2024-03-11 | 2024-06-03 | 0.0 | 0.0 | 0.0 | N-5 | 83.47 | No | - | 198.77 | 6.84 | 0.31 | 0.21 | 0.00 | 23.62 | -55.5 | 0.15
2024-03-11 | 2024-06-17 | 1.5 | 0.0 | 0.0 | N-4 | 83.5 | No | - | 205.53 | 7.01 | 0.32 | 0.12 | 0.00 | 23.44 | -10.6 | 0.15
2024-03-11 | 2024-07-01 | 0.0 | 0.0 | 0.0 | N-3 | 83.5 | No | - | 195.01 | 6.89 | 0.30 | 0.20 | 0.04 | 23.65 | -41.7 | 0.14
2024-03-11 | 2024-07-15 | 0.0 | 0.0 | 0.0 | N-3 | 83.48 | No | - | 197.63 | 7.26 | 0.30 | 0.16 | 0.00 | 23.53 | -61.2 | 0.15
2024-03-11 | 2024-08-05 | 0.0 | 0.0 | 0.0 | N-3 | 83.54 | No | - | 191.65 | 6.97 | 0.29 | 0.17 | 0.00 | 23.69 | -48.1 | 0.14
2024-03-11 | 2024-08-22 | 0.0 | 0.0 | 0.0 | N-5 | 83.5 | No | - | 190.69 | 7.00 | 0.29 | 0.19 | 0.00 | 23.83 | -14.4 | 0.14
2024-03-11 | 2024-09-03 | 0.0 | 0.0 | 0.0 | N-5 | 83.41 | No | - | 193.80 | 7.01 | 0.30 | 0.20 | 0.00 | 23.85 | -37.0 | 0.14
2024-03-11 | 2024-09-16 | 0.0 | 0.0 | 0.0 | 252094 | 83.32 | No | - | 183.82 | 7.15 | 0.28 | 0.14 | 0.00 | 23.63 | -2.4 | 0.14
2024-03-11 | 2024-10-21 | 0.0 | 0.0 | 0.0 | N-4 | 83.39 | No | - | 211.54 | 6.99 | 0.33 | 0.28 | 0.00 | 23.64 | -66.4 | 0.16
2024-03-11 | 2024-11-04 | 0.0 | 0.0 | 0.0 | N-1 | 83.24 | No | - | 194.20 | 7.23 | 0.30 | 0.11 | 0.00 | 23.35 | -185.3 | 0.14
2024-03-11 | 2024-11-18 | 0.0 | 0.0 | 0.0 | N-5 | 83.15 | No | - | 224.51 | 6.97 | 0.35 | 0.11 | 0.04 | 23.57 | -118.4 | 0.17
2024-03-11 | 2024-12-02 | 0.0 | 0.0 | 0.0 | N-3 | 83.33 | No | - | 187.87 | 6.98 | 0.29 | 0.11 | 0.30 | 23.51 | -119.8 | 0.14
2024-03-11 | 2024-12-16 | 0.0 | 0.0 | 0.0 | N-3 | 83.35 | No | - | 194.82 | 6.95 | 0.30 | 0.08 | 0.13 | 23.49 | -175.9 | 0.14
| RHMW02 Headspace and Product Gauging | [7 empty] | RHMW02 Parameter Readings
WEEK | DATE | AMBIENT | TOP-OF-CASING HEADSPACE | GROUNDWATER HEADSPACE | TAPE | DTW (Raw) | PRODUCT? | THICKNESS | TDS | pH | Sp. Cond. | D.O. | Turbidity | TEMP | ORP | SAL
|  | (ppmv) | (ppmv) | (ppmv) | (Serial #) | (ft btoc) | (Yes/No) | (ft) | (ppm) |  | (mS/cm) | (mg/L) | (NTU) | (°C) | (Mv) | (psu)
06/12/2023 | 06/15/2023 | 0.0 | 0.0 | - | N-3 | 86.59 | No | - | 356.53 | 6.71 | 0.55 | 0.13 | 0.07 | 24.54 | -304.3 | 0.27
07/03/2023 | 07/05/2023 | 0.0 | 0.0 | - | N-3 | 86.86 | No | - | 350.94 | 6.68 | 0.54 | 0.13 | 0.23 | 24.44 | -219.5 | 0.26
07/31/2023 | 08/03/2023 | 0.0 | 0.2 | - | N-4 | 86.94 | No | - | 324.18 | 6.63 | 0.50 | 0.25 | 0.22 | 24.57 | -277.4 | 0.24
09/04/2023 | 09/07/2023 | 0.0 | 0.0 | - | N-4 | 87.08 | No | - | 302.89 | 6.62 | 0.47 | 0.25 | 0.04 | 24.65 | -285.2 | 0.23
10/02/2023 | 10/06/2023 | 0.0 | 0.0 | - | N-4 | 87.22 | No | - | 338.50 | 6.66 | 0.52 | 0.17 | 0.25 | 24.44 | -165.3 | 0.25
10/16/2023 | 10/20/2023 | 0.0 | 0.0 | - | N-4 | 87.23 | No | - | 323.46 | 6.66 | 0.50 | 0.07 | 0.05 | 24.38 | -151.8 | 0.24
10/23/2023 | 10/27/2023 | 0.0 | 0.0 | - | N-4 | 87.26 | No | - | 315.94 | 6.70 | 0.49 | 0.12 | 0.18 | 24.61 | -180.7 | 0.24
10/30/2023 | 11/03/2023 | 0.0 | 0.0 | - | N-4 | 87.27 | No | - | 314.77 | 6.72 | 0.48 | 0.06 | 0.21 | 24.45 | -161.6 | 0.24
11/06/2023 | 11/07/2023 | 0.0 | 0.3 | - | N-5 | 87.22 | No | - | 318.40 | 6.72 | 0.50 | 0.10 | 0.23 | 24.52 | -111.3 | 0.24
2023-11-13 | 2023-11-17 | 0.0 | 0.0 | - | N-4 | 87.25 | No | - | 324.11 | 6.76 | 0.50 | 0.09 | 0.23 | 24.56 | -90.1 | 0.24
2023-11-20 | 2023-11-21 | 0.0 | 0.0 | - | N-3 | 87.29 | No | - | 311.03 | 6.68 | 0.48 | 0.05 | 0.14 | 24.47 | -250.5 | 0.23
2023-11-27 | 2023-12-01 | 0.0 | 0.1 | - | N-4 | 87.19 | No | - | 322.85 | 6.73 | 0.50 | 0.04 | 0.08 | 24.58 | -131.0 | 0.24
2023-12-04 | 2023-12-08 | 0.0 | 0.1 | - | N-4 | 87.08 | No | - | 321.90 | 6.70 | 0.50 | 0.07 | 0.02 | 24.52 | -87.6 | 0.24
2023-12-11 | 2023-12-15 | 0.0 | 0.3 | - | N-3 | 87.08 | No | - | 304.96 | 6.72 | 0.47 | 0.05 | 0.51 | 24.43 | -97.2 | 0.23
2023-12-18 | 2023-12-19 | 0.0 | 0.0 | - | N-5 | 87.19 | No | - | 291.53 | 6.76 | 0.45 | 0.04 | 0.00 | 24.48 | -126.5 | 0.22
2023-12-25 | 2023-12-26 | 0.0 | 0.0 | - | N-5 | 87.02 | No | - | 303.79 | 6.79 | 0.47 | 0.06 | 0.09 | 24.53 | -79.6 | 0.23
2024-01-01 | 2024-01-05 | 0.0 | 0.0 | - | N-4 | 87.05 | No | - | 305.70 | 6.67 | 0.47 | 0.05 | 0.12 | 24.55 | -175.4 | 0.23
2024-01-08 | 2024-01-12 | 0.0 | 0.0 | - | N-3 | 86.95 | No | - | 306.17 | 6.70 | 0.47 | 0.08 | 0.46 | 24.46 | -108.6 | 0.23
2024-01-15 | 2024-01-19 | 0.0 | 0.2 | - | N-4 | 86.98 | No | - | 297.82 | 6.73 | 0.46 | 0.06 | 0.93 | 24.49 | -93.0 | 0.22
2024-02-12 | 2024-02-13 | 0.0 | 0.0 | - | N-4 | 86.89 | No | - | 297.98 | 6.72 | 0.46 | 0.09 | 0.78 | 24.44 | -138.3 | 0.22
2024-03-11 | 2024-03-15 | 0.0 | 0.0 | - | N-4 | 86.91 | No | - | 303.37 | 6.61 | 0.47 | 0.09 | 0.33 | 24.47 | -139.5 | 0.23
2024-03-11 | 2024-04-04 | 0.0 | 0.0 | - | N-5 | 86.96 | No | - | 298.27 | 6.62 | 0.46 | 0.08 | 0.14 | 24.46 | -67.2 | 0.22
2024-03-11 | 2024-05-09 | 0.0 | 0.5 | 0.0 | N-4 | 86.71 | No | - | 315.56 | 6.69 | 0.49 | 0.08 | 0.25 | 24.47 | -114.2 | 0.24
2024-03-11 | 2024-05-23 | 0.0 | 0.0 | 0.0 | N-5 | 86.53 | No | - | 368.04 | 6.69 | 0.57 | 0.02 | 0.76 | 24.47 | -176.7 | 0.28
2024-03-11 | 2024-06-03 | 0.0 | 0.0 | 0.0 | N-5 | 86.38 | No | - | 324.06 | 6.68 | 0.50 | 0.08 | 0.00 | 24.48 | -126.5 | 0.24
2024-03-11 | 2024-06-17 | 0.0 | 0.0 | 0.0 | N-4 | 86.42 | No | - | 331.02 | 6.76 | 0.51 | 0.03 | 0.00 | 24.47 | -76.7 | 0.25
2024-03-11 | 2024-07-01 | 0.0 | 0.0 | 0.0 | N-3 | 86.45 | No | - | 318.54 | 6.72 | 0.49 | 0.07 | 0.08 | 24.48 | -136.6 | 0.24
2024-03-11 | 2024-07-15 | 0.0 | 1.0 | 0.0 | N-3 | 86.42 | No | - | 313.71 | 6.83 | 0.48 | 0.09 | 0.00 | 24.53 | -95.4 | 0.23
2024-03-11 | 2024-08-05 | 0.0 | 0.0 | 0.0 | N-3 | 86.47 | No | - | 309.05 | 6.73 | 0.48 | 0.06 | 0.00 | 24.52 | -123.3 | 0.23
2024-03-11 | 2024-08-22 | 0.0 | 0.0 | 0.0 | N-5 | 86.45 | No | - | 325.59 | 6.73 | 0.50 | 0.06 | 0.00 | 24.60 | -65.4 | 0.24
2024-03-11 | 2024-09-03 | 0.0 | 0.0 | 0.0 | N-5 | 86.29 | No | - | 303.60 | 6.83 | 0.47 | 0.08 | 0.11 | 24.63 | -89.4 | 0.23
2024-03-11 | 2024-09-26 | 0.0 | 0.7 | 0.0 | N-5 | 86.29 | No | - | 340.95 | 6.72 | 0.52 | 0.11 | 0.00 | 24.52 | -113.1 | 0.26
2024-03-11 | 2024-10-07 | 0.0 | 0.1 | 0.0 | N-4 | 86.34 | No | - | 338.92 | 6.83 | 0.52 | 0.11 | 0.10 | 24.68 | -13.7 | 0.25
2024-03-11 | 2024-10-21 | 0.0 | 0.0 | 0.0 | N-4 | 86.29 | No | - | 332.62 | 6.76 | 0.51 | 0.01 | 0.00 | 24.22 | -107.5 | 0.25
2024-03-11 | 2024-11-04 | 0.0 | 0.0 | 0.0 | N-1 | 86.18 | No | - | 304.17 | 6.97 | 0.47 | 0.08 | 0.45 | 24.33 | -226.9 | 0.23
2024-03-11 | 2024-11-18 | 0.0 | 0.0 | 0.0 | N-5 | 86.03 | No | - | 358.68 | 6.75 | 0.55 | 0.07 | 0.15 | 24.57 | -190.8 | 0.27
2024-03-11 | 2024-12-02 | 0.0 | 0.0 | 0.0 | N-3 | 86.22 | No | - | 315.37 | 6.73 | 0.49 | 0.05 | 0.42 | 24.29 | -182.1 | 0.24
2024-03-11 | 2024-12-16 | 0.0 | 0.0 | 0.0 | N-3 | 86.25 | No | - | 318.69 | 6.71 | 0.49 | 0.06 | 0.15 | 24.41 | -272.3 | 0.24
| RHMW03 Headspace and Product Gauging | [7 empty] | RHMW03 Parameter Readings
WEEK | DATE | AMBIENT | TOP-OF-CASING HEADSPACE | GROUNDWATER HEADSPACE | TAPE | DTW (Raw) | PRODUCT? | THICKNESS | TDS | pH | Sp. Cond. | D.O. | Turbidity | TEMP | ORP | SAL
|  | (ppmv) | (ppmv) | (ppmv) | (Serial #) | (ft btoc) | (Yes/No) | (ft) | (ppm) |  | (mS/cm) | (mg/L) | (NTU) | (°C) | (Mv) | (psu)
06/12/2023 | 06/14/2023 | 0.0 | 0.0 | - | N-3 | 102.78 | No | - | 517.88 | 6.74 | 0.80 | 0.64 | 0.09 | 27.25 | 105.1 | 0.39
07/03/2023 | 07/05/2023 | 0.0 | 0.0 | - | N-3 | 103.03 | No | - | 492.15 | 7.03 | 0.76 | 0.47 | 0.17 | 27.24 | 0.6 | 0.37
07/31/2023 | 08/03/2023 | 0.0 | 1.1 | - | N-4 | 103.16 | No | - | 494.95 | 6.75 | 0.76 | 0.58 | 0.48 | 27.39 | 15.6 | 0.38
09/04/2023 | 09/07/2023 | 0.0 | 0.0 | - | N-4 | 103.31 | No | - | 471.47 | 6.77 | 0.73 | 0.75 | 11.52 | 27.88 | 20.1 | 0.36
10/02/2023 | 10/06/2023 | 0.0 | 0.0 | - | N-4 | 103.43 | No | - | 524.24 | 6.82 | 0.81 | 0.56 | 0.79 | 27.40 | 186.3 | 0.40
10/16/2023 | 10/20/2023 | 0.0 | 0.0 | - | N-4 | 103.44 | No | - | 505.37 | 6.83 | 0.78 | 0.43 | 0.30 | 27.31 | 155.7 | 0.38
10/23/2023 | 10/27/2023 | 0.0 | 0.0 | - | N-4 | 103.48 | No | - | 490.43 | 6.90 | 0.75 | 0.47 | 5.12 | 27.06 | 126.2 | 0.37
10/30/2023 | 11/03/2023 | 0.0 | 0.0 | - | N-4 | 103.5 | No | - | 493.61 | 6.88 | 0.76 | 0.49 | 0.70 | 27.51 | 128.7 | 0.37
11/06/2023 | 11/10/2023 | 0.0 | 0.0 | - | N-4 | 103.47 | No | - | 497.46 | 6.83 | 0.80 | 0.40 | 0.83 | 27.49 | 186.5 | 0.38
2023-11-13 | 2023-11-17 | 0.0 | 0.1 | - | N-5 | 103.44 | No | - | 494.06 | 6.87 | 0.76 | 0.47 | 0.17 | 27.17 | 188.7 | 0.38
2023-11-20 | 2023-11-21 | 0.0 | 0.0 | - | N-3 | 103.48 | No | - | 504.39 | 6.88 | 0.78 | 0.46 | 1.56 | 27.05 | 165.0 | 0.38
2023-11-27 | 2023-11-28 | 0.0 | 0.0 | - | N-5 | 103.4 | No | - | 498.98 | 6.86 | 0.77 | 0.45 | 0.03 | 27.01 | 200.6 | 0.38
2023-12-04 | 2023-12-08 | 0.0 | 0.0 | - | N-4 | 103.29 | No | - | 531.82 | 6.84 | 0.82 | 0.42 | 0.52 | 27.39 | 155.0 | 0.41
2023-12-11 | 2023-12-12 | 0.0 | 0.0 | - | N-6 | 103.33 | No | - | 491.15 | 6.86 | 0.76 | 0.45 | 0.42 | 27.12 | 187.8 | 0.37
2023-12-18 | 2023-12-19 | 0.0 | 0.0 | - | N-4 | 103.37 | No | - | 491.00 | 6.90 | 0.76 | 0.58 | 0.68 | 27.20 | 186.0 | 0.37
2023-12-25 | 2023-12-26 | 0.0 | 0.0 | - | N-4 | 103.29 | No | - | 479.47 | 6.77 | 0.74 | 0.42 | 0.00 | 27.24 | 146.7 | 0.36
2024-01-01 | 2024-01-02 | 0.1 | 0.1 | - | N-5 | 103.28 | No | - | 505.08 | 6.83 | 0.78 | 0.47 | 0.76 | 27.23 | 224.9 | 0.38
2024-01-08 | 2024-01-09 | 0.0 | 0.0 | - | N-5 | 103.19 | No | - | 506.80 | 6.85 | 0.78 | 1.47 | 0.40 | 27.11 | 259.0 | 0.39
2024-01-15 | 2024-01-16 | 0.0 | 2.0 | - | N-4 | 103.17 | No | - | 422.40 | 6.77 | 0.65 | 1.01 | 0.00 | 27.35 | 220.3 | 0.35
2024-02-05 | 2024-02-06 | 0.0 | 3.1 | - | N-4 | 103.18 | No | - | 492.00 | 6.80 | 0.76 | 0.63 | 0.80 | 27.20 | 157.2 | 0.37
2024-03-11 | 2024-03-13 | 0.0 | 0.0 | - | N-5 | 103.1 | No | - | 503.61 | 6.77 | 0.77 | 0.52 | 0.85 | 27.33 | 198.6 | 0.38
2024-03-11 | 2024-04-04 | 0.0 | 0.0 | - | N-5 | 103.2 | No | - | 485.80 | 6.73 | 0.75 | 0.50 | 0.67 | 27.03 | 147.3 | 0.37
2024-03-11 | 2024-05-07 | 0.0 | 0.0 | 0.0 | N-4 | 103.03 | No | - | 524.96 | 6.86 | 0.81 | 0.53 | 0.10 | 27.14 | 203.7 | 0.40
2024-03-11 | 2024-05-23 | 0.0 | 0.0 | 0.0 | N-5 | 102.76 | No | - | 545.02 | 6.84 | 0.84 | 0.49 | 0.00 | 27.17 | 159.1 | 0.42
2024-03-11 | 2024-06-04 | 0.0 | 0.0 | 0.0 | N-4 | 102.63 | No | - | 480.73 | 6.80 | 0.74 | 0.58 | 0.25 | 27.32 | 250.6 | 0.36
2024-03-11 | 2024-06-19 | 0.0 | 0.2 | 0.0 | N-3 | 102.73 | No | - | 486.13 | 6.79 | 0.75 | 0.63 | 0.80 | 27.19 | 229.8 | 0.37
2024-03-11 | 2024-07-02 | 0.0 | 1.7 | 0.0 | N-5 | 102.78 | No | - | 514.65 | 6.81 | 0.79 | 0.59 | 0.38 | 27.08 | 203.3 | 0.39
2024-03-11 | 2024-07-16 | 0.0 | 4.1 | 0.0 | N-3 | 102.76 | No | - | 539.65 | 6.82 | 0.83 | 0.54 | 0.10 | 27.18 | 156.0 | 0.41
2024-03-11 | 2024-08-06 | 0.2 | 0.4 | 0.0 | N-5 | 102.79 | No | - | 503.44 | 6.84 | 0.77 | 0.63 | 0.11 | 27.13 | 187.7 | 0.38
2024-03-11 | 2024-08-20 | 0.0 | 5.0 | 0.0 | N-5 | 102.81 | No | - | 482.71 | 6.82 | 0.74 | 0.56 | 0.22 | 27.37 | 190.0 | 0.37
2024-03-11 | 2024-09-03 | 0.0 | 0.0 | 0.0 | N-5 | 102.5 | No | - | 507.29 | 6.85 | 0.78 | 0.50 | 0.45 | 27.37 | 159.8 | 0.39
2024-03-11 | 2024-09-26 | 0.0 | 0.6 | 0.0 | N-5 | 102.5 | No | - | 516.41 | 6.85 | 0.79 | 0.58 | 2.13 | 27.15 | 132.0 | 0.39
2024-03-11 | 2024-10-08 | 0.2 | 1.4 | 0.0 | N-4 | 102.73 | No | - | 551.40 | 6.74 | 0.85 | 0.51 | 3.15 | 27.13 | 241.6 | 0.42
2024-03-11 | 2024-10-22 | 0.0 | 0.0 | 0.0 | N-4 | 102.67 | No | - | 546.47 | 6.78 | 0.84 | 0.57 | 1.90 | 27.27 | 155.6 | 0.42
2024-03-11 | 2024-11-05 | 0.0 | 0.0 | 0.0 | N-3 | 102.55 | No | - | 500.78 | 6.84 | 0.77 | 0.49 | 0.32 | 27.20 | 61.4 | 0.38
2024-03-11 | 2024-11-19 | 0.0 | 0.0 | 0.0 | N-3 | 102.45 | No | - | 484.64 | 6.76 | 0.75 | 0.44 | 3.42 | 26.98 | 152.1 | 0.37
2024-03-11 | 2024-12-06 | 0.0 | 0.0 | 0.0 | N-3 | 102.34 | No | - | 490.69 | 6.79 | 0.75 | 0.48 | 0.46 | 26.89 | 169.4 | 0.37
2024-03-11 | 2024-12-17 | 0.0 | 0.0 | 0.0 | N-3 | 102.4 | No | - | 508.14 | 6.79 | 0.78 | 0.49 | 0.77 | 27.32 | 188.4 | 0.39
| RHMW04 Headspace and Product Gauging | [7 empty] | RHMW04 Parameter Readings
WEEK | DATE | AMBIENT | TOP-OF-CASING HEADSPACE | GROUNDWATER HEADSPACE | TAPE | DTW (Raw) | PRODUCT? | THICKNESS | TDS | pH | Sp. Cond. | D.O. | Turbidity | TEMP | ORP | SAL
|  | (ppmv) | (ppmv) | (ppmv) | (Serial #) | (ft btoc) | (Yes/No) | (ft) | (ppm) |  | (mS/cm) | (mg/L) | (NTU) | (°C) | (Mv) | (psu)
06/12/2023 | 06/14/2023 | 0.0 | 0.0 | - | N-4 | 294.14 | No | - | 271.24 | 7.38 | 0.42 | 8.58 | 0.00 | 23.64 | 174.2 | 0.20
07/03/2023 | 07/05/2023 | 0.0 | 0.0 | - | N-4 | 294.42 | No | - | 249.10 | 7.31 | 0.38 | 8.45 | 0.85 | 24.35 | 209.9 | 0.19
07/31/2023 | 08/04/2023 | 0.0 | 0.0 | - | N-4 | 294.48 | No | - | 267.44 | 7.39 | 0.41 | 8.79 | 0.20 | 23.11 | 151.8 | 0.20
09/04/2023 | 09/08/2023 | 0.0 | 0.0 | - | N-5 | 294.58 | No | - | 274.70 | 7.32 | 0.42 | 8.99 | 0.12 | 23.57 | 119.1 | 0.20
10/02/2023 | 10/06/2023 | 0.0 | 0.0 | - | N-6 | 294.71 | No | - | 269.08 | 7.38 | 0.41 | 9.08 | 0.42 | 23.50 | 256.1 | 0.20
10/23/2023 | 10/23/2023 | 0.0 | 0.0 | - | N-3 | 294.7 | No | - | 273.99 | 7.42 | 0.42 | 8.68 | 0.00 | 23.35 | 157.7 | 0.20
10/30/2023 | 10/30/2023 | 0.0 | 0.0 | - | N-6 | 294.77 | No | - | 270.27 | 7.45 | 0.42 | 9.36 | 0.00 | 22.72 | 287.1 | 0.20
11/06/2023 | 11/07/2023 | 0.0 | 0.5 | - | N-6 | 294.76 | No | - | 275.76 | 7.41 | 0.40 | 8.70 | 0.00 | 23.31 | 300.3 | 0.21
2023-11-13 | 2023-11-13 | 0.0 | 0.0 | - | N-4 | 294.81 | No | - | 288.06 | 7.42 | 0.44 | 9.31 | 0.00 | 23.06 | 296.0 | 0.22
2023-11-20 | 2023-11-20 | 0.0 | 0.0 | - | N-5 | 294.76 | No | - | 269.86 | 7.42 | 0.42 | 8.72 | 0.07 | 22.76 | 292.3 | 0.20
2023-11-27 | 2023-11-27 | 0.0 | 0.0 | - | N-6 | 294.75 | No | - | 265.54 | 7.40 | 0.41 | 8.74 | 0.00 | 22.94 | 257.1 | 0.20
2023-12-04 | 2023-12-05 | 0.0 | 0.5 | - | N-4 | 294.71 | No | - | 275.52 | 7.44 | 0.42 | 8.79 | 0.00 | 22.88 | 293.4 | 0.21
2023-12-11 | 2023-12-11 | 0.0 | 0.1 | - | N-4 | 294.64 | No | - | 263.29 | 7.34 | 0.41 | 8.65 | 0.40 | 23.11 | 277.5 | 0.20
2023-12-18 | 2023-12-18 | 0.0 | 0.0 | - | N-4 | 294.65 | No | - | 298.42 | 7.44 | 0.46 | 8.75 | 0.00 | 22.08 | 273.7 | 0.22
2023-12-25 | 2023-12-27 | 0.0 | 0.0 | - | N-6 | 294.54 | No | - | 254.99 | 7.51 | 0.39 | 8.68 | 0.11 | 22.38 | 223.0 | 0.19
2024-01-01 | 2024-01-02 | 0.0 | 0.0 | - | N-3 | 294.51 | No | - | 272.04 | 7.49 | 0.42 | 8.74 | 0.00 | 22.44 | 256.8 | 0.20
2024-01-08 | 2024-01-08 | 0.0 | 0.0 | - | N-3 | 294.45 | No | - | 264.38 | 7.36 | 0.41 | 9.04 | 0.12 | 22.62 | 158.4 | 0.20
2024-01-15 | 2024-01-15 | 0.0 | 0.0 | - | N-5 | 294.42 | No | - | 275.86 | 7.34 | 0.42 | 8.86 | 0.15 | 21.87 | 245.0 | 0.21
2024-02-12 | 2024-02-12 | 0.0 | 0.0 | - | N-4 | 294.4 | No | - | 256.64 | 7.34 | 0.39 | 8.78 | 0.36 | 22.97 | 268.8 | 0.19
2024-03-18 | 2024-03-22 | 0.0 | 0.0 | - | N-4 | 294.48 | No | - | 285.57 | 7.29 | 0.44 | 8.68 | 0.00 | 22.58 | 276.8 | 0.21
2024-03-18 | 2024-04-08 | 0.0 | 0.0 | - | N-6 | 294.48 | No | - | 265.87 | 7.31 | 0.41 | 8.68 | 0.24 | 22.35 | 245.0 | 0.20
2024-03-18 | 2024-05-14 | 0.0 | 0.1 | 0.0 | N-5 | 294.27 | No | - | 264.27 | 7.33 | 0.41 | 8.77 | 0.25 | 22.84 | 289.7 | 0.20
2024-03-18 | 2024-05-31 | 0.0 | 0.0 | 0.0 | N-3 | 294.04 | No | - | 264.04 | 7.32 | 0.41 | 8.69 | 0.28 | 23.23 | 272.9 | 0.20
2024-03-18 | 2024-06-11 | 0.0 | 0.0 | 0.0 | N-4 | 294.08 | No | - | 259.40 | 7.59 | 0.40 | 8.77 | 0.00 | 23.26 | 253.3 | 0.19
2024-03-18 | 2024-06-25 | 0.0 | 0.0 | 0.0 | N-4 | 294.5 | No | - | 287.48 | 7.36 | 0.44 | 8.64 | 0.00 | 24.18 | 288.9 | 0.21
2024-03-18 | 2024-07-09 | 0.0 | 0.0 | 0.0 | N-5 | 294.05 | No | - | 287.07 | 7.42 | 0.44 | 8.79 | 0.00 | 23.32 | 346.4 | 0.21
2024-03-18 | 2024-07-23 | 0.0 | 0.0 | 0.0 | N-3 | 294.04 | No | - | 259.15 | 7.43 | 0.40 | 8.69 | 0.00 | 23.26 | 230.4 | 0.19
2024-03-18 | 2024-08-13 | 0.0 | 0.0 | 0.0 | N-3 | 294 | No | - | 272.77 | 7.46 | 0.42 | 8.70 | 0.31 | 23.70 | 254.0 | 0.20
2024-03-18 | 2024-08-27 | 0.0 | 0.0 | 0.0 | N-3 | 294.04 | No | - | 273.41 | 7.43 | 0.42 | 8.29 | 0.29 | 23.47 | 224.8 | 0.20
2024-03-18 | 2024-09-20 | 0.0 | 0.0 | 0.0 | 252094 | 293.89 | No | - | 268.11 | 7.40 | 0.41 | 8.75 | 0.00 | 23.35 | 241.0 | 0.20
2024-03-18 | 2024-10-15 | 0.0 | 0.0 | 0.0 | N-3 | 293.85 | No | - | 251.46 | 7.95 | 0.39 | 8.85 | 0.00 | 23.24 | 233.1 | 0.19
2024-03-18 | 2024-11-11 | 0.0 | 0.0 | 0.0 | N-3 | 293.74 | No | - | 271.05 | 7.42 | 0.42 | 8.89 | 0.00 | 22.94 | 125.9 | 0.20
2024-03-18 | 2024-11-26 | 0.0 | 0.0 | 0.0 | N-3 | 293.71 | No | - | 276.36 | 7.36 | 0.43 | 8.80 | 0.15 | 22.94 | 142.1 | 0.21
2024-03-18 | 2024-12-10 | 0.0 | 0.0 | 0.0 | N-3 | 293.72 | No | - | 265.21 | 7.34 | 0.41 | 8.79 | 0.00 | 23.11 | 195.9 | 0.20
2024-03-18 | 2024-12-24 | 0.0 | 0.0 | 0.0 | N-4 | 293.8 | No | - | 271.14 | 7.19 | 0.42 | 8.78 | 0.00 | 22.88 | 261.9 | 0.20
| RHMW05 Headspace and Product Gauging | [7 empty] | RHMW05 Parameter Readings
WEEK | DATE | AMBIENT | TOP-OF-CASING HEADSPACE | GROUNDWATER HEADSPACE | TAPE | DTW (Raw) | PRODUCT? | THICKNESS | TDS | pH | Sp. Cond. | D.O. | Turbidity | TEMP | ORP | SAL
|  | (ppmv) | (ppmv) | (ppmv) | (Serial #) | (ft btoc) | (Yes/No) | (ft) | (ppm) |  | (mS/cm) | (mg/L) | (NTU) | (°C) | (Mv) | (psu)
06/12/2023 | 06/15/2023 | 0.0 | 0.0 | - | N-4 | 83.29 | No | - | 208.34 | 7.47 | 0.32 | 7.71 | 0.45 | 23.32 | 146.5 | 0.15
07/03/2023 | 07/07/2023 | 0.1 | 0.1 | - | N-3 | 83.53 | No | - | 209.61 | 7.42 | 0.32 | 7.76 | 0.21 | 23.48 | 283.8 | 0.16
07/31/2023 | 08/01/2023 | 0.0 | 0.0 | - | N-4 | 83.64 | No | - | 210.76 | 7.39 | 0.32 | 7.29 | 3.99 | 26.66 | 111.5 | 0.16
09/04/2023 | 09/05/2023 | 0.0 | 0.0 | - | N-4 | 83.74 | No | - | 210.74 | 7.39 | 0.32 | 7.72 | 0.58 | 22.98 | 173.6 | 0.16
10/02/2023 | 10/04/2023 | 0.0 | 0.0 | - | N-4 | 83.9 | No | - | 204.75 | 7.33 | 0.31 | 7.57 | 0.56 | 22.86 | 219.4 | 0.15
10/16/2023 | 10/17/2023 | 0.0 | 0.0 | - | N-5 | 83.88 | No | - | 204.06 | 7.51 | 0.31 | 7.49 | 1.26 | 22.86 | 124.0 | 0.15
10/23/2023 | 10/24/2023 | 0.0 | 0.0 | - | N-3 | 83.91 | No | - | 203.64 | 7.43 | 0.31 | 7.81 | 0.54 | 23.08 | 248.1 | 0.15
10/30/2023 | 10/31/2023 | 0.0 | 0.0 | - | N-4 | 83.92 | No | - | 204.60 | 7.48 | 0.31 | 7.48 | 0.18 | 23.09 | 310.5 | 0.15
11/06/2023 | 11/10/2023 | 0.0 | 0.0 | - | N-3 | 83.93 | No | - | 204.12 | 7.52 | 0.30 | 7.50 | 0.09 | 23.09 | 273.0 | 0.15
2023-11-13 | 2023-11-14 | 0.0 | 0.0 | - | N-5 | 83.92 | No | - | 209.12 | 7.43 | 0.32 | 7.57 | 0.28 | 23.10 | 304.9 | 0.15
2023-11-20 | 2023-11-21 | 0.0 | 0.0 | - | N-4 | 83.99 | No | - | 196.17 | 7.45 | 0.30 | 7.46 | 1.12 | 22.99 | 267.5 | 0.15
2023-11-27 | 2023-11-28 | 0.0 | 0.0 | - | N-4 | 83.9 | No | - | 202.96 | 7.47 | 0.31 | 7.47 | 0.31 | 22.95 | 288.3 | 0.15
2023-12-04 | 2023-12-05 | 0.0 | 0.0 | - | N-5 | 83.8 | No | - | 199.00 | 7.42 | 0.31 | 7.49 | 2.30 | 23.12 | 269.7 | 0.15
2023-12-11 | 2023-12-12 | 0.0 | 0.0 | - | N-3 | 83.77 | No | - | 189.42 | 7.46 | 0.29 | 7.49 | 0.17 | 22.89 | 281.7 | 0.14
2023-12-18 | 2023-12-22 | 0.0 | 0.0 | - | N-4 | 83.75 | No | - | 201.99 | 7.49 | 0.31 | 7.49 | 0.01 | 22.90 | 221.5 | 0.15
2023-12-25 | 2023-12-29 | 0.0 | 0.0 | - | N-4 | 83.73 | No | - | 207.90 | 7.50 | 0.32 | 7.57 | 1.39 | 22.94 | 261.8 | 0.15
2024-01-01 | 2024-01-02 | 0.0 | 0.0 | - | N-5 | 83.74 | No | - | 196.77 | 7.42 | 0.30 | 7.61 | 0.23 | 22.97 | 291.0 | 0.15
2024-01-08 | 2024-01-09 | 0.0 | 0.6 | - | N-5 | 83.64 | No | - | 216.36 | 7.38 | 0.33 | 7.60 | 0.37 | 22.91 | 298.4 | 0.16
2024-01-15 | 2024-01-16 | 0.1 | 0.1 | - | N-6 | 83.61 | No | - | 206.82 | 7.36 | 0.32 | 7.55 | 0.55 | 22.91 | 325.5 | 0.15
2024-02-12 | 2024-02-16 | 0.0 | 0.0 | - | N-5 | 83.58 | No | - | 197.76 | 7.41 | 0.30 | 7.04 | 0.55 | 22.93 | 242.4 | 0.15
2024-03-11 | 2024-03-12 | 0.0 | 0.0 | - | N-5 | 83.59 | No | - | 198.40 | 7.37 | 0.31 | 7.76 | 0.18 | 22.98 | 272.8 | 0.15
2024-03-11 | 2024-04-03 | 0.1 | 0.0 | - | N-5 | 83.69 | No | - | 209.16 | 7.23 | 0.32 | 7.76 | 0.13 | 22.63 | 247.2 | 0.15
2024-03-11 | 2024-05-08 | 0.0 | 0.0 | 0.0 | N-5 | 83.45 | No | - | 193.21 | 7.38 | 0.30 | 7.59 | 0.31 | 23.04 | 246.1 | 0.14
2024-03-11 | 2024-05-22 | 0.0 | 0.0 | 0.0 | N-3 | 83.16 | No | - | 218.59 | 7.43 | 0.34 | 7.65 | 0.40 | 23.05 | 333.5 | 0.16
2024-03-11 | 2024-06-05 | 0.0 | 0.0 | 0.0 | N-4 | 83.23 | No | - | 198.92 | 7.31 | 0.31 | 7.60 | 0.22 | 23.19 | 248.9 | 0.15
2024-03-11 | 2024-06-18 | 0.1 | 0.0 | 0.0 | N-4 | 83.11 | No | - | 198.26 | 7.65 | 0.31 | 7.57 | 0.16 | 23.00 | 200.8 | 0.15
2024-03-11 | 2024-07-03 | 0.0 | 0.0 | 0.0 | N-4 | 83.3 | No | - | 205.19 | 7.33 | 0.32 | 7.55 | 0.00 | 23.10 | 304.9 | 0.15
2024-03-11 | 2024-07-17 | 0.0 | 0.0 | 0.0 | N-3 | 83.21 | No | - | 214.86 | 7.44 | 0.33 | 7.89 | 0.00 | 23.02 | 254.5 | 0.16
2024-03-11 | 2024-08-07 | 0.0 | 0.0 | 0.0 | N-5 | 83.22 | No | - | 219.11 | 7.39 | 0.34 | 7.47 | 0.94 | 23.32 | 279.3 | 0.16
2024-03-11 | 2024-08-21 | 0.0 | 0.0 | 0.0 | N-5 | 83.21 | No | - | 220.01 | 7.45 | 0.34 | 7.73 | 0.00 | 23.20 | 340.9 | 0.16
2024-03-11 | 2024-09-05 | 0.0 | 0.0 | 0.0 | N-5 | 83.03 | No | - | 197.68 | 7.48 | 0.30 | 7.62 | 0.00 | 23.11 | 216.8 | 0.15
2024-03-11 | 2024-09-18 | 0.0 | 0.0 | 0.0 | 252094 | 83.06 | No | - | 225.08 | 7.40 | 0.35 | 7.70 | 0.00 | 23.11 | 311.9 | 0.17
2024-03-11 | 2024-10-23 | 0.0 | 0.0 | 0.0 | N-4 | 83.03 | No | - | 220.00 | 7.40 | 0.34 | 7.63 | 1.43 | 23.09 | 148.2 | 0.16
2024-03-11 | 2024-11-06 | 0.0 | 0.0 | 0.0 | N-4 | 83 | No | - | 198.25 | 7.62 | 0.31 | 7.60 | 0.34 | 23.21 | 61.3 | 0.15
2024-03-11 | 2024-11-20 | 0.0 | 0.0 | 0.0 | N-5 | 82.85 | No | - | 212.46 | 7.43 | 0.33 | 7.59 | 0.68 | 23.00 | 155.7 | 0.16
2024-03-11 | 2024-12-04 | 0.0 | 0.0 | 0.0 | N-3 | 82.69 | No | - | 203.95 | 7.38 | 0.31 | 7.65 | 1.03 | 22.87 | 227.7 | 0.15
2024-03-11 | 2024-12-18 | 0.0 | 0.0 | 0.0 | N-3 | 82.73 | No | - | 208.48 | 7.33 | 0.32 | 7.62 | 1.80 | 22.94 | 252.1 | 0.15
| RHMW06 Headspace and Product Gauging | [7 empty] | RHMW06 Parameter Readings
WEEK | DATE | AMBIENT | TOP-OF-CASING HEADSPACE | GROUNDWATER HEADSPACE | TAPE | DTW (Raw) | PRODUCT? | THICKNESS | TDS | pH | Sp. Cond. | D.O. | Turbidity | TEMP | ORP | SAL
|  | (ppmv) | (ppmv) | (ppmv) | (Serial #) | (ft btoc) | (Yes/No) | (ft) | (ppm) |  | (mS/cm) | (mg/L) | (NTU) | (°C) | (Mv) | (psu)
06/12/2023 | 06/14/2023 | 0.0 | 0.0 | - | N-4 | 241.12 | No | - | 1096.38 | 6.76 | 1.69 | 6.26 | 0.00 | 25.76 | 178.1 | 0.86
07/03/2023 | 07/05/2023 | 0.0 | 0.0 | - | N-4 | 241.37 | No | - | 1077.26 | 6.81 | 1.66 | 6.49 | 0.75 | 26.29 | 200.5 | 0.85
07/31/2023 | 08/04/2023 | 0.0 | 0.0 | - | N-4 | 241.45 | No | - | 1117.89 | 6.85 | 1.72 | 6.56 | 0.46 | 25.02 | 144.7 | 0.88
09/04/2023 | 09/08/2023 | 0.0 | 0.0 | - | N-5 | 241.53 | No | - | 1134.76 | 6.53 | 1.75 | 6.55 | 0.17 | 25.97 | 106.3 | 0.89
10/02/2023 | 10/06/2023 | 0.0 | 0.0 | - | N-6 | 241.63 | No | - | 1116.33 | 6.83 | 1.72 | 6.91 | 0.55 | 24.81 | 268.9 | 0.88
10/23/2023 | 10/23/2023 | 0.0 | 0.0 | - | N-3 | 241.66 | No | - | 1138.31 | 6.88 | 1.75 | 6.62 | 0.00 | 25.03 | 150.0 | 0.90
10/30/2023 | 10/30/2023 | 0.0 | 0.0 | - | N-6 | 241.71 | No | - | 1107.47 | 6.95 | 1.70 | 7.08 | 0.19 | 25.19 | 307.9 | 0.87
11/06/2023 | 11/07/2023 | 0.0 | 1.2 | - | N-6 | 241.69 | No | - | 1131.54 | 6.91 | 1.70 | 6.50 | 0.00 | 24.64 | 283.4 | 0.89
2023-11-13 | 2023-11-13 | 0.0 | 0.0 | - | N-4 | 241.75 | No | - | 1182.08 | 6.92 | 1.82 | 6.97 | 0.00 | 24.61 | 297.0 | 0.93
2023-11-20 | 2023-11-20 | 0.0 | 0.1 | - | N-5 | 241.75 | No | - | 1114.77 | 6.91 | 1.72 | 6.56 | 0.13 | 24.24 | 285.1 | 0.88
2023-11-27 | 2023-11-27 | 0.0 | 0.0 | - | N-6 | 241.68 | No | - | 1085.06 | 6.92 | 1.67 | 6.57 | 0.04 | 24.39 | 263.8 | 0.85
2023-12-04 | 2023-12-05 | 0.0 | 0.0 | - | N-4 | 241.61 | No | - | 1129.26 | 6.93 | 1.74 | 6.53 | 0.00 | 24.18 | 277.2 | 0.89
2023-12-11 | 2023-12-11 | 0.0 | 0.4 | - | N-4 | 241.59 | No | - | 1047.61 | 6.90 | 1.61 | 6.48 | 0.45 | 24.33 | 271.5 | 0.82
2023-12-18 | 2023-12-18 | 0.0 | 0.0 | - | N-4 | 241.58 | No | - | 1191.20 | 6.92 | 1.83 | 6.42 | 0.03 | 23.91 | 283.1 | 0.94
2023-12-25 | 2023-12-27 | 0.0 | 0.0 | - | N-6 | 241.47 | No | - | 1030.07 | 6.97 | 1.58 | 6.56 | 0.23 | 24.33 | 240.5 | 0.81
2024-01-01 | 2024-01-02 | 0.0 | 0.0 | - | N-3 | 241.43 | No | - | 1053.68 | 6.96 | 1.62 | 6.51 | 0.00 | 24.01 | 244.4 | 0.83
2024-01-08 | 2024-01-08 | 0.0 | 0.0 | - | N-3 | 241.4 | No | - | 1066.36 | 6.89 | 1.64 | 6.92 | 0.00 | 24.09 | 152.8 | 0.84
2024-01-15 | 2024-01-15 | 0.0 | 0.0 | - | N-5 | 241.38 | No | - | 1085.11 | 6.90 | 1.67 | 6.61 | 0.36 | 23.98 | 258.0 | 0.85
2024-02-05 | 2024-02-05 | 0.0 | 0.0 | - | N-6 | 241.39 | No | - | 1108.73 | 6.95 | 1.71 | 6.65 | 0.36 | 25.01 | 280.7 | 0.87
2024-03-11 | 2024-03-11 | 0.0 | 0.0 | - | N-6 | 241.39 | No | - | 1093.77 | 6.92 | 1.68 | 6.74 | 0.22 | 24.13 | 235.3 | 0.86
2024-03-11 | 2024-04-01 | 0.0 | 0.0 | - | N-6 | 241.41 | No | - | 1056.32 | 6.99 | 1.63 | 6.73 | 0.08 | 24.91 | 211.0 | 0.83
2024-03-11 | 2024-05-06 | 0.1 | 0.1 | 0.0 | N-5 | 241.2 | No | - | 1055.36 | 6.88 | 1.62 | 6.86 | 0.26 | 24.67 | 219.3 | 0.83
2024-03-11 | 2024-05-20 | 0.0 | 0.0 | 0.0 | N-3 | 240.93 | No | - | 1027.79 | 7.09 | 1.58 | 6.61 | 0.14 | 25.67 | 330.3 | 0.81
| 2024-06-06 | 0.0 | 0.0 | 0.0 | N-4 | 241.03 | No | - | 1002.43 | 6.77 | 1.54 | 6.76 | 0.45 | 25.77 | 265.8 | 0.79
| 2024-06-20 | 0.0 | 0.0 | 0.0 | N-3 | 241.03 | No | - | 1009.84 | 6.87 | 1.55 | 6.51 | 0.78 | 25.19 | 295.6 | 0.79
| 2024-07-01 | 0.0 | 0.0 | 0.0 | N-5 | 240.96 | No | - | 1076.06 | 6.90 | 1.66 | 6.64 | 0.00 | 25.32 | 300.3 | 0.85
| 2024-07-18 | 0.0 | 0.0 | 0.0 | N-3 | 240.95 | No | - | 1133.40 | 6.90 | 1.74 | 6.70 | 0.00 | 25.31 | 279.4 | 0.89
| 2024-08-08 | 0.0 | 0.0 | 0.0 | N-5 | 240.96 | No | - | 1087.09 | 6.93 | 1.67 | 7.09 | 0.13 | 25.06 | 198.2 | 0.85
| 2024-08-22 | 0.0 | 0.0 | 0.0 | N-3 | 240.92 | No | - | 1137.77 | 6.88 | 1.75 | 6.62 | 0.00 | 25.49 | 359.5 | 0.90
| 2024-08-22 | 0.0 | 0.0 | 0.0 | N-3 | 240.92 | No | - | 1137.77 | 6.88 | 1.75 | 6.62 | 0.00 | 25.49 | 359.5 | 0.90
| 2024-09-19 | 0.0 | 0.0 | 0.0 | 288404 | 240.83 | No | - | 1055.62 | 6.78 | 1.62 | 6.64 | 1.19 | 24.61 | 326.2 | 0.83
| 2024-10-10 | 0.0 | 0.0 | 0.0 | N-5 | 240.82 | No | - | 1102.52 | 6.88 | 1.70 | 6.75 | 0.07 | 24.98 | 245.0 | 0.87
| 2024-10-24 | 0.0 | 0.0 | 0.0 | N-4 | 240.87 | No | - | 1071.18 | 6.84 | 1.65 | 6.71 | 0.13 | 24.77 | 186.4 | 0.84
| 2024-11-07 | 0.0 | 0.0 | 0.0 | N-4 | 240.78 | No | - | 1037.37 | 6.82 | 1.60 | 6.57 | 0.00 | 24.39 | 121.1 | 0.81
| 2024-11-21 | 0.0 | 0.0 | 0.0 | N-3 | 240.61 | No | - | 1000.26 | 6.92 | 1.54 | 7.12 | 0.61 | 24.75 | 247.2 | 0.78
| 2024-12-05 | 0.0 | 0.0 | 0.0 | N-4 | 240.7 | No | - | 1062.33 | 6.71 | 1.63 | 6.86 | 0.12 | 24.74 | 215.5 | 0.83
| 2024-12-19 | 0.0 | 0.0 | 0.0 | N-5 | 240.69 | No | - | 1067.19 | 6.85 | 1.64 | 6.75 | 0.58 | 25.52 | 255.6 | 0.84
| RHMW08 Headspace and Product Gauging | [7 empty] | RHMW08 Parameter Readings
WEEK | DATE | AMBIENT | TOP-OF-CASING HEADSPACE | GROUNDWATER HEADSPACE | TAPE | DTW (Raw) | PRODUCT? | THICKNESS | TDS | pH | Sp. Cond. | D.O. | Turbidity | TEMP | ORP | SAL
|  | (ppmv) | (ppmv) | (ppmv) | (Serial #) | (ft btoc) | (Yes/No) | (ft) | (ppm) |  | (mS/cm) | (mg/L) | (NTU) | (°C) | (Mv) | (psu)
06/12/2023 | 06/16/2023 | 0.0 | 0.0 | - | N-6 | 292.53 | No | - | 483.85 | 7.84 | 0.74 | 1.40 | 0.29 | 25.39 | -261.2 | 0.37
07/03/2023 | 07/06/2023 | 0.0 | 0.0 | - | N-4 | 292.91 | No | - | 408.10 | 7.86 | 0.63 | 1.49 | 16.68 | 24.73 | -117.5 | 0.31
07/31/2023 | 08/02/2023 | 0.0 | 0.0 | - | N-5 | 292.91 | No | - | 445.37 | 7.82 | 0.69 | 2.23 | 0.00 | 27.93 | 113.9 | 0.34
09/04/2023 | 09/06/2023 | 0.0 | 0.0 | - | N-5 | 293.03 | No | - | 442.92 | 7.93 | 0.68 | 3.38 | 0.21 | 25.83 | 126.5 | 0.34
10/02/2023 | 10/04/2023 | 0.0 | 0.0 | - | N-6 | 293.09 | No | - | 410.51 | 7.94 | 0.63 | 3.48 | 0.74 | 25.48 | 186.5 | 0.31
10/16/2023 | 10/18/2023 | 0.0 | 0.0 | - | N-4 | 293.17 | No | - | 426.94 | 7.85 | 0.66 | 1.84 | 0.73 | 25.73 | 175.2 | 0.32
10/23/2023 | 10/25/2023 | 0.0 | 0.0 | - | N-3 | 293.12 | No | - | 432.63 | 7.89 | 0.67 | 2.05 | 0.17 | 26.14 | 71.9 | 0.33
10/30/2023 | 11/01/2023 | 0.0 | 0.0 | - | N-4 | 293.16 | No | - | 424.31 | 7.98 | 0.65 | 2.39 | 0.08 | 26.18 | 201.8 | 0.32
11/06/2023 | 11/10/2023 | 0.0 | 0.0 | - | N-6 | 293.18 | No | - | 436.49 | 8.01 | 0.70 | 2.60 | 0.00 | 25.28 | 162.9 | 0.33
2023-11-13 | 2023-11-14 | 0.0 | 0.0 | - | N-3 | 293.14 | No | - | 426.63 | 8.01 | 0.66 | 2.82 | 0.01 | 25.03 | 212.7 | 0.32
2023-11-20 | 2023-11-20 | 0.0 | 0.0 | - | N-4 | 293.23 | No | - | 421.92 | 8.02 | 0.65 | 3.03 | 0.33 | 24.80 | 209.9 | 0.32
2023-11-27 | 2023-11-28 | 0.0 | 0.0 | - | N-6 | 293.14 | No | - | 412.66 | 8.02 | 0.63 | 3.07 | 0.00 | 24.67 | 206.5 | 0.31
2023-12-04 | 2023-12-04 | 0.0 | 0.0 | - | N-5 | 293.05 | No | - | 427.98 | 8.08 | 0.66 | 3.05 | 0.34 | 25.45 | 201.2 | 0.32
2023-12-11 | 2023-12-11 | 0.0 | 0.0 | - | N-5 | 293.02 | No | - | 421.38 | 8.00 | 0.65 | 2.44 | 0.17 | 25.41 | 204.5 | 0.32
2023-12-18 | 2023-12-18 | 0.0 | 0.0 | - | N-5 | 293.02 | No | - | 420.65 | 7.97 | 0.65 | 2.94 | 0.21 | 24.52 | 168.2 | 0.32
2023-12-25 | 2023-12-26 | 0.0 | 0.0 | - | N-6 | 292.99 | No | - | 431.60 | 7.80 | 0.66 | 0.36 | 0.71 | 24.23 | -78.9 | 0.33
2024-01-01 | 2024-01-03 | 0.0 | 0.0 | - | N-6 | 292.86 | No | - | 425.61 | 7.80 | 0.65 | 0.48 | 0.06 | 25.69 | 41.6 | 0.32
2024-01-08 | 2024-01-08 | 0.4 | 0.0 | - | N-5 | 292.88 | No | - | 438.31 | 7.55 | 0.67 | 0.94 | 0.00 | 24.54 | 182.0 | 0.33
2024-01-15 | 2024-01-15 | 0.0 | 0.0 | - | N-3 | 292.84 | No | - | 447.10 | 7.53 | 0.69 | 1.58 | 0.44 | 24.78 | 228.6 | 0.34
2024-02-05 | 2024-02-05 | 0.0 | 0.0 | - | N-6 | 292.87 | No | - | 458.02 | 8.01 | 0.70 | 2.40 | 0.48 | 25.01 | 213.1 | 0.35
2024-03-11 | 2024-03-11 | 0.0 | 0.0 | - | N-6 | 292.89 | No | - | 428.83 | 8.00 | 0.66 | 3.15 | 0.22 | 24.45 | 156.5 | 0.32
2024-03-11 | 2024-04-01 | 0.0 | 0.0 | - | N-6 | 292.91 | No | - | 408.79 | 7.96 | 0.63 | 3.50 | 0.57 | 24.80 | 136.2 | 0.31
2024-03-11 | 2024-05-06 | 0.0 | 0.0 | 0.0 | N-5 | 292.61 | No | - | 417.52 | 8.01 | 0.64 | 4.00 | 0.71 | 24.95 | 112.0 | 0.32
2024-03-11 | 2024-05-20 | 0.0 | 0.0 | 0.0 | N-3 | 292.37 | No | - | 427.65 | 8.02 | 0.66 | 3.68 | 0.00 | 24.97 | 250.9 | 0.32
2024-03-11 | 2024-06-03 | 0.0 | 0.1 | 0.0 | N-3 | 292.29 | No | - | 451.69 | 7.90 | 0.69 | 2.35 | 0.00 | 25.63 | 195.5 | 0.34
2024-03-11 | 2024-06-17 | 0.0 | 0.0 | 0.0 | N-5 | 292.32 | No | - | 417.89 | 8.04 | 0.64 | 0.39 | 0.00 | 25.14 | -188.8 | 0.32
2024-03-11 | 2024-07-01 | 0.0 | 0.0 | 0.0 | N-5 | 292.35 | No | - | 453.34 | 7.82 | 0.70 | 0.80 | 0.00 | 24.91 | 171.2 | 0.34
2024-03-11 | 2024-07-15 | 0.0 | 0.0 | 0.0 | N-5 | 292.37 | No | - | 459.03 | 7.89 | 0.71 | 2.25 | 0.26 | 27.54 | 119.1 | 0.35
2024-03-11 | 2024-08-05 | 0.0 | 0.0 | 0.0 | N-6 | 292.4 | No | - | 464.64 | 7.96 | 0.71 | 2.70 | 0.32 | 25.97 | 180.3 | 0.35
2024-03-11 | 2024-08-21 | 0.0 | 0.0 | 0.0 | N-4 | 292.53 | No | - | 439.46 | 7.43 | 0.68 | 3.09 | 0.29 | 25.52 | 156.8 | 0.33
2024-03-11 | 2024-09-03 | 0.0 | 0.0 | 0.0 | N-3 | 292.19 | No | - | 436.15 | 7.97 | 0.67 | 3.40 | 0.16 | 25.61 | 155.0 | 0.33
2024-03-11 | 2024-09-16 | 0.0 | 0.0 | 0.0 | 288404 | 292.26 | No | - | 466.23 | 7.94 | 0.72 | 2.72 | 0.00 | 25.97 | 232.4 | 0.35
2024-03-11 | 2024-10-01 | 0.0 | 0.0 | 0.0 | N-5 | 292.37 | No | - | 430.67 | 7.97 | 0.66 | 3.41 | 0.19 | 25.40 | 204.6 | 0.33
2024-03-11 | 2024-10-21 | 0.0 | 0.0 | 0.0 | N-3 | 292.16 | No | - | 438.23 | 7.76 | 0.67 | 2.23 | 0.03 | 25.39 | 213.9 | 0.33
2024-03-11 | 2024-11-04 | 0.0 | 0.0 | 0.0 | N-4 | 292.15 | No | - | 462.69 | 8.05 | 0.71 | 1.83 | 1.86 | 25.00 | 85.6 | 0.35
2024-03-11 | 2024-11-18 | 0.0 | 0.0 | 0.0 | N-3 | 292.18 | No | - | 408.57 | 8.10 | 0.63 | 0.57 | 0.35 | 24.76 | -197.6 | 0.31
2024-03-11 | 2024-12-02 | 0.0 | 0.0 | 0.0 | N-5 | 292.24 | No | - | 453.84 | 7.95 | 0.70 | 0.33 | 0.35 | 24.51 | -14.3 | 0.34
2024-03-11 | 2024-12-16 | 0.0 | 0.0 | 0.0 | N-5 | 292.23 | No | - | 435.26 | 7.96 | 0.67 | 0.68 | 0.38 | 25.04 | 76.9 | 0.33
| RHMW09 Headspace and Product Gauging | [7 empty] | RHMW09 Parameter Readings
WEEK | DATE | AMBIENT | TOP-OF-CASING HEADSPACE | GROUNDWATER HEADSPACE | TAPE | DTW (Raw) | PRODUCT? | THICKNESS | TDS | pH | Sp. Cond. | D.O. | Turbidity | TEMP | ORP | SAL
|  | (ppmv) | (ppmv) | (ppmv) | (Serial #) | (ft btoc) | (Yes/No) | (ft) | (ppm) |  | (mS/cm) | (mg/L) | (NTU) | (°C) | (Mv) | (psu)
06/12/2023 | 06/13/2023 | 0.0 | 0.0 | - | N-6 | 377.55 | No | - | 216.76 | 7.47 | 0.33 | 7.94 | 0.28 | 24.03 | 158.2 | 0.16
07/03/2023 | 07/06/2023 | 0.0 | 0.0 | - | N-6 | 377.97 | No | - | 211.56 | 7.48 | 0.33 | 8.39 | 0.24 | 24.07 | 137.6 | 0.16
07/31/2023 | 08/01/2023 | 0.0 | 0.0 | - | N-5 | 377.98 | No | - | 215.24 | 7.49 | 0.33 | 8.64 | 0.05 | 24.46 | 79.5 | 0.16
09/04/2023 | 09/05/2023 | 0.0 | 0.0 | - | N-5 | 378.09 | No | - | 204.33 | 6.91 | 0.31 | 8.61 | 0.18 | 25.48 | 116.5 | 0.15
10/02/2023 | 10/05/2023 | 0.0 | 0.0 | - | N-6 | 378.23 | No | - | 210.56 | 7.23 | 0.32 | 8.58 | 0.00 | 25.23 | 249.0 | 0.16
10/23/2023 | 10/24/2023 | 0.0 | 0.0 | - | N-6 | 378.31 | No | - | 206.24 | 7.54 | 0.32 | 8.55 | 0.00 | 24.71 | 156.3 | 0.15
10/30/2023 | 10/30/2023 | 0.0 | 0.0 | - | N-4 | 378.3 | No | - | 206.18 | 7.59 | 0.32 | 8.61 | 0.28 | 24.55 | 264.0 | 0.15
11/06/2023 | 11/06/2023 | 0.0 | 0.0 | - | N-6 | 378.34 | No | - | 213.21 | 7.49 | 0.30 | 8.60 | 3.54 | 24.50 | 278.0 | 0.16
2023-11-13 | 2023-11-14 | 0.0 | 0.0 | - | N-6 | 378.3 | No | - | 218.26 | 7.52 | 0.34 | 8.48 | 0.10 | 25.25 | 301.1 | 0.16
2023-11-20 | 2023-11-20 | 0.0 | 0.0 | - | N-3 | 378.32 | No | - | 210.51 | 7.50 | 0.32 | 8.57 | 0.52 | 24.01 | 184.0 | 0.16
2023-11-27 | 2023-11-27 | 0.0 | 0.0 | - | N-5 | 378.23 | No | - | 216.77 | 7.51 | 0.33 | 8.60 | 1.10 | 24.10 | 280.9 | 0.16
2023-12-04 | 2023-12-04 | 0.0 | 0.0 | - | N-4 | 378.23 | No | - | 207.15 | 7.56 | 0.32 | 8.60 | 0.59 | 23.93 | 262.4 | 0.15
| 2023-12-12 | 0.0 | 0.0 | - | N-4 | 378.18 | No | - | 210.95 | 7.49 | 0.32 | 8.55 | 0.44 | 23.99 | 285.6 | 0.16
2023-12-18 | 2023-12-19 | 0.0 | 0.0 | - | N-6 | 378.18 | No | - | 209.99 | 7.55 | 0.32 | 8.61 | 0.00 | 23.48 | 291.1 | 0.16
2023-12-25 | 2023-12-27 | 0.0 | 0.0 | - | N-4 | 378.1 | No | - | 206.81 | 7.55 | 0.32 | 9.22 | 0.00 | 23.53 | 267.7 | 0.15
2024-01-01 | 2024-01-04 | 0.0 | 0.0 | - | N-4 | 378.09 | No | - | 216.68 | 7.34 | 0.33 | 8.58 | 0.32 | 24.21 | 283.0 | 0.16
2024-01-08 | 2024-01-09 | 0.0 | 0.0 | - | N-4 | 378.05 | No | - | 216.58 | 7.49 | 0.33 | 8.59 | 0.04 | 23.63 | 255.4 | 0.16
2024-01-15 | 2024-01-16 | 0.0 | 0.0 | - | N-5 | 377.94 | No | - | 216.96 | 7.56 | 0.33 | 8.60 | 0.00 | 23.86 | 232.5 | 0.16
2024-02-05 | 2024-02-07 | 0.0 | 0.1 | - | N-4 | 378.02 | No | - | 213.83 | 7.47 | 0.33 | 8.55 | 0.95 | 24.13 | 223.7 | 0.16
2024-03-11 | 2024-03-12 | 0.0 | 0.0 | - | N-6 | 377.98 | No | - | 207.41 | 6.96 | 0.32 | 8.51 | 0.87 | 24.53 | 243.2 | 0.15
2024-03-11 | 2024-04-02 | 0.0 | 0.1 | - | N-6 | 378.02 | No | - | 198.21 | 7.39 | 0.30 | 8.57 | 0.11 | 23.92 | 273.7 | 0.15
2024-03-11 | 2024-05-07 | 0.0 | 0.0 | 0.0 | N-5 | 377.88 | No | - | 205.47 | 7.50 | 0.32 | 8.64 | 0.23 | 23.92 | 271.9 | 0.15
2024-03-11 | 2024-05-21 | 0.0 | 0.0 | 0.0 | N-5 | 377.49 | No | - | 199.93 | 7.32 | 0.31 | 8.63 | 0.00 | 24.00 | 338.4 | 0.15
2024-03-11 | 2024-06-04 | 0.0 | 0.0 | 0.0 | N-3 | 377.47 | No | - | 211.60 | 6.97 | 0.33 | 8.64 | 0.25 | 25.01 | 259.4 | 0.16
2024-03-11 | 2024-06-18 | 0.0 | 0.0 | 0.0 | N-3 | 377.55 | No | - | 221.70 | 7.55 | 0.34 | 8.44 | 0.10 | 24.39 | 266.5 | 0.16
2024-03-11 | 2024-07-02 | 0.0 | 0.0 | 0.0 | N-3 | 377.66 | No | - | 201.70 | 7.63 | 0.31 | 8.52 | 0.13 | 24.97 | 252.3 | 0.15
2024-03-11 | 2024-07-16 | 0.0 | 0.0 | 0.0 | N-4 | 377.68 | No | - | 210.13 | 7.56 | 0.32 | 8.86 | 0.13 | 24.28 | 195.8 | 0.16
2024-03-11 | 2024-08-09 | 0.0 | 0.0 | 0.0 | N-3 | 377.44 | No | - | 225.39 | 7.49 | 0.35 | 8.41 | 0.00 | 25.12 | 305.5 | 0.17
2024-03-11 | 2024-08-23 | 0.0 | 0.0 | 0.0 | N-3 | 377.5 | No | - | 225.03 | 7.55 | 0.35 | 8.61 | 0.00 | 24.72 | 351.8 | 0.17
2024-03-11 | 2024-09-09 | 0.0 | 0.0 | 0.0 | N-5 | 377.34 | No | - | 205.03 | 7.54 | 0.32 | 8.48 | 1.14 | 25.83 | 253.3 | 0.15
2024-03-11 | 2024-09-20 | 0.0 | 0.0 | 0.0 | 252094 | 377.4 | No | - | 216.37 | 7.52 | 0.33 | 8.49 | 0.47 | 25.46 | 238.9 | 0.16
2024-03-11 | 2024-10-01 | 0.0 | 0.0 | 0.0 | N-5 | 377.45 | No | - | 209.39 | 7.49 | 0.32 | 8.57 | 0.30 | 25.15 | 277.9 | 0.16
2024-03-11 | 2024-10-25 | 0.0 | 0.0 | 0.0 | N-4 | 377.42 | No | - | 199.10 | 7.60 | 0.31 | 8.44 | 0.00 | 24.88 | 96.5 | 0.15
2024-03-11 | 2024-11-08 | 0.0 | 0.0 | 0.0 | N-3 | 377.26 | No | - | 295.53 | 7.52 | 0.45 | 8.54 | 0.00 | 23.91 | 152.2 | 0.22
2024-03-11 | 2024-11-22 | 0.0 | 0.0 | 0.0 | N-3 | 377.17 | No | - | 216.62 | 7.48 | 0.33 | 8.52 | 0.46 | 24.43 | 168.0 | 0.16
2024-03-11 | 2024-12-06 | 0.0 | 0.0 | 0.0 | N-4 | 377.27 | No | - | 214.30 | 7.43 | 0.33 | 8.36 | 0.21 | 24.42 | 153.4 | 0.16
2024-03-11 | 2024-12-20 | 0.0 | 0.0 | 0.0 | N-3 | 377.18 | No | - | 231.31 | 7.44 | 0.36 | 8.02 | 8.09 | 24.23 | 77.7 | 0.17
| RHMW10 Headspace and Product Gauging | [7 empty] | RHMW10 Parameter Readings
WEEK | DATE | AMBIENT | TOP-OF-CASING HEADSPACE | GROUNDWATER HEADSPACE | TAPE | DTW (Raw) | PRODUCT? | THICKNESS | TDS | pH | Sp. Cond. | D.O. | Turbidity | TEMP | ORP | SAL
|  | (ppmv) | (ppmv) | (ppmv) | (Serial #) | (ft btoc) | (Yes/No) | (ft) | (ppm) |  | (mS/cm) | (mg/L) | (NTU) | (°C) | (Mv) | (psu)
06/12/2023 | 06/14/2023 | 0.0 | 0.0 | - | N-6 | 477.69 | No | - | 208.33 | 7.55 | 0.32 | 8.48 | 0.00 | 24.83 | 261.5 | 0.15
07/03/2023 | 07/05/2023 | 0.0 | 0.0 | - | N-6 | 477.99 | No | - | 181.56 | 7.32 | 0.28 | 8.51 | 0.00 | 24.48 | 120.7 | 0.13
07/31/2023 | 08/01/2023 | 0.0 | 0.0 | - | N-6 | 478.05 | No | - | 177.50 | 7.50 | 0.27 | 8.50 | 0.07 | 24.53 | 104.2 | 0.13
09/04/2023 | 09/05/2023 | 0.0 | 0.1 | - | N-6 | 478.13 | No | - | 191.61 | 7.38 | 0.29 | 8.48 | 0.20 | 25.51 | 131.2 | 0.14
10/02/2023 | 10/05/2023 | 0.0 | 0.0 | - | N-3 | 478.2 | No | - | 191.35 | 7.44 | 0.29 | 8.52 | 0.44 | 24.43 | 280.8 | 0.14
10/23/2023 | 10/26/2023 | 0.0 | 0.0 | - | N-4 | 478.34 | No | - | 180.49 | 7.52 | 0.28 | 8.49 | 0.21 | 25.18 | 249.6 | 0.13
10/30/2023 | 10/31/2023 | 0.0 | 0.0 | - | N-6 | 478.32 | No | - | 180.56 | 7.50 | 0.28 | 8.44 | 0.00 | 24.44 | 287.4 | 0.13
11/06/2023 | 11/10/2023 | 0.0 | 0.0 | - | N-6 | 478.34 | No | - | 184.99 | 7.49 | 0.30 | 8.50 | 0.10 | 25.32 | 241.7 | 0.14
2023-11-13 | 2023-11-13 | 0.0 | 0.0 | - | N-6 | 478.35 | No | - | 175.00 | 7.50 | 0.27 | 8.77 | 0.00 | 25.04 | 305.8 | 0.13
2023-11-20 | 2023-11-21 | 0.0 | 0.0 | - | N-6 | 478.26 | No | - | 183.94 | 7.38 | 0.28 | 8.33 | 0.41 | 23.82 | 200.8 | 0.14
2023-11-27 | 2023-11-29 | 0.0 | 0.0 | - | N-3 | 478.21 | No | - | 177.90 | 7.58 | 0.27 | 8.10 | 0.47 | 23.75 | 246.4 | 0.13
2023-12-04 | 2023-12-05 | 0.0 | 0.0 | - | N-6 | 478.2 | No | - | 182.52 | 7.45 | 0.28 | 8.42 | 0.00 | 24.14 | 273.4 | 0.13
2023-12-11 | 2023-12-13 | 0.0 | 0.0 | - | N-6 | 478.2 | No | - | NC | 7.47 | NC | 8.51 | 0.00 | 23.65 | 309.9 | NC
2023-12-18 | 2023-12-20 | 0.0 | 0.0 | - | N-6 | 478.16 | No | - | 179.14 | 7.46 | 0.28 | 8.54 | 0.65 | 23.39 | 239.9 | 0.13
2023-12-25 | 2023-12-28 | 0.0 | 0.0 | - | N-4 | 478.13 | No | - | 177.19 | 7.45 | 0.27 | 8.16 | 0.02 | 24.14 | 272.4 | 0.13
2024-01-01 | 2024-01-02 | 0.0 | 0.0 | - | N-4 | 478.19 | No | - | 179.26 | 7.47 | 0.28 | 8.11 | 0.00 | 24.44 | 287.3 | 0.13
2024-01-08 | 2024-01-10 | 0.0 | 0.0 | - | N-6 | 478.05 | No | - | 179.58 | 7.45 | 0.28 | 8.38 | 0.14 | 23.69 | 142.8 | 0.13
2024-01-15 | 2024-01-17 | 0.0 | 0.2 | - | N-6 | 478 | No | - | 188.49 | 7.35 | 0.29 | 8.15 | 0.30 | 24.23 | 267.9 | 0.14
2024-02-05 | 2024-02-07 | 0.0 | 0.2 | - | N-5 | 477.97 | No | - | 173.74 | 7.43 | 0.27 | 8.58 | 0.63 | 24.21 | 227.3 | 0.13
2024-03-11 | 2024-03-15 | 0.0 | 0.0 | - | N-5 | 477.96 | No | - | 179.01 | 7.35 | 0.28 | 8.49 | 0.40 | 24.84 | 303.2 | 0.13
2024-03-11 | 2024-04-05 | 0.0 | 0.0 | - | N-6 | 478.08 | No | - | 206.28 | 7.43 | 0.32 | 8.53 | 0.00 | 23.21 | 298.3 | 0.15
2024-03-11 | 2024-05-10 | 0.0 | 0.0 | 0.0 | N-5 | 477.75 | No | - | 185.78 | 7.37 | 0.29 | 8.57 | 0.80 | 24.39 | 304.0 | 0.14
2024-03-11 | 2024-05-24 | 0.0 | 0.0 | 0.0 | N-3 | 477.65 | No | - | 177.18 | 6.90 | 0.27 | 8.55 | 0.37 | 24.97 | 252.2 | 0.13
2024-03-11 | 2024-06-07 | 0.0 | 0.0 | 0.0 | N-4 | 477.6 | No | - | 193.15 | 7.32 | 0.30 | 8.24 | 0.47 | 25.13 | 308.9 | 0.14
2024-03-11 | 2024-06-21 | 0.0 | 0.0 | 0.0 | N-4 | 477.63 | No | - | 175.29 | 7.26 | 0.27 | 8.43 | 0.00 | 24.56 | 303.3 | 0.13
2024-03-11 | 2024-07-05 | 0.0 | 0.0 | 0.0 | N-5 | 477.57 | No | - | 200.12 | 7.41 | 0.31 | 8.43 | 0.01 | 24.15 | 254.6 | 0.15
2024-03-11 | 2024-07-19 | 0.0 | 0.0 | 0.0 | N-4 | 477.63 | No | - | 194.73 | 7.47 | 0.30 | 8.38 | 0.00 | 24.83 | 282.7 | 0.14
2024-03-11 | 2024-08-09 | 0.0 | 0.0 | 0.0 | N-5 | 477.53 | No | - | 177.27 | 7.62 | 0.27 | 8.22 | 0.04 | 25.44 | 243.3 | 0.13
2024-03-11 | 2024-08-23 | 0.0 | 0.0 | 0.0 | N-5 | 477.53 | No | - | 178.43 | 7.49 | 0.27 | 8.56 | 0.00 | 24.28 | 351.0 | 0.13
2024-03-11 | 2024-09-06 | 0.0 | 0.0 | 0.0 | N-5 | 477.4 | No | - | 197.35 | 7.47 | 0.30 | 8.40 | 0.00 | 24.73 | 316.6 | 0.15
2024-03-11 | 2024-10-11 | 0.0 | 0.0 | 0.0 | N-5 | 477.42 | No | - | 196.91 | 7.50 | 0.30 | 8.60 | 0.00 | 24.56 | 287.8 | 0.15
2024-03-11 | 2024-10-25 | 0.0 | 0.0 | 0.0 | N-5 | 477.41 | No | - | 181.54 | 7.44 | 0.28 | 8.26 | 0.53 | 25.38 | 183.1 | 0.13
2024-03-11 | 2024-11-08 | 0.0 | 0.0 | 0.0 | N-5 | 477.31 | No | - | 176.46 | 7.61 | 0.27 | 8.26 | 0.22 | 24.01 | 133.3 | 0.13
2024-03-11 | 2024-11-21 | 0.0 | 0.0 | 0.0 | N-3 | 477.14 | No | - | 178.22 | 7.45 | 0.27 | 8.88 | 0.55 | 24.23 | 224.6 | 0.13
2024-03-11 | 2024-12-03 | 0.0 | 0.0 | 0.0 | N-3 | 477.19 | No | - | 184.31 | 7.38 | 0.28 | 8.18 | 0.45 | 24.54 | 266.4 | 0.14
2024-03-11 | 2024-12-19 | 0.0 | 0.0 | 0.0 | N-5 | 477.26 | No | - | 189.35 | 7.40 | 0.29 | 8.28 | 0.50 | 24.51 | 257.3 | 0.14
| RHMW11-05 Headspace and Product Gauging | [7 empty] | RHMW11-05 Parameter Readings
WEEK | DATE | AMBIENT | TOP-OF-CASING HEADSPACE | GROUNDWATER HEADSPACE | TAPE | DTW (Raw) | PRODUCT? | THICKNESS | TDS | pH | Sp. Cond. | D.O. | Turbidity | TEMP | ORP | SAL
|  | (ppmv) | (ppmv) | (ppmv) | (Serial #) | (ft btoc) | (Yes/No) | (ft) | (ppm) |  | (mS/cm) | (mg/L) | (NTU) | (°C) | (Mv) | (psu)
06/05/2023 | 06/08/2023 | 0.0 | 0.0 | 0.0 | - | - | No | - | 277.69 | 8.05 | 0.43 | 0.98 | 0.35 | 24.29 | -34.3 | 0.21
07/03/2023 | 07/06/2023 | 0.0 | 0.0 | 0.0 | - | - | No | - | 262.18 | 7.93 | 0.40 | 0.77 | 0.42 | 25.11 | -13.2 | 0.20
07/31/2023 | 08/02/2023 | 0.0 | 0.0 | 0.0 | - | - | No | - | 267.90 | 8.09 | 0.41 | 1.63 | 0.00 | 27.75 | -121.6 | 0.20
09/04/2023 | 09/06/2023 | 0.0 | 0.0 | 0.0 | - | - | No | - | 270.36 | 7.95 | 0.42 | 0.67 | 0.26 | 26.99 | -228.5 | 0.20
10/02/2023 | 10/02/2023 | 0.0 | 0.0 | 0.0 | - | - | No | - | 263.84 | 8.17 | 0.41 | 0.82 | 0.48 | 25.49 | -156.5 | 0.20
10/23/2023 | 10/24/2023 | 0.0 | 0.0 | 0.0 | - | - | No | - | 272.67 | 8.04 | 0.42 | 1.14 | 0.49 | 26.85 | 54.6 | 0.20
10/30/2023 | 10/30/2023 | 0.0 | 0.0 | 0.0 | - | - | No | - | 267.53 | 8.10 | 0.41 | 1.76 | 1.07 | 25.25 | -10.5 | 0.20
11/06/2023 | 11/06/2023 | 0.0 | 0.0 | 0.0 | - | - | No | - | 258.20 | 7.97 | 0.40 | 1.10 | 4.51 | 26.68 | 23.8 | 0.19
2023-11-13 | 2023-11-15 | 0.0 | 0.0 | 0.0 | - | - | No | - | 266.53 | 8.06 | 0.41 | 1.04 | 0.47 | 23.98 | -22.6 | 0.20
2023-11-20 | 2023-11-22 | 0.0 | 0.0 | 0.0 | - | - | No | - | 252.24 | 8.07 | 0.39 | 0.85 | 0.13 | 26.14 | -100.1 | 0.19
2023-11-27 | 2023-11-27 | 0.0 | 0.0 | 0.0 | - | - | No | - | 264.08 | 8.10 | 0.41 | 0.81 | 0.00 | 25.43 | -43.9 | 0.20
2023-12-04 | 2023-12-04 | 0.0 | 0.0 | 0.0 | - | - | No | - | 257.79 | 8.12 | 0.40 | 3.10 | 0.82 | 24.82 | 13.2 | 0.19
2023-12-11 | 2023-12-13 | 0.0 | 0.0 | 0.0 | - | - | No | - | 263.80 | 7.99 | 0.41 | 1.60 | 0.93 | 23.89 | 34.7 | 0.20
2023-12-18 | 2023-12-20 | 0.0 | 0.0 | 0.0 | - | - | No | - | 248.11 | 8.16 | 0.38 | 1.20 | 0.00 | 22.32 | -6.8 | 0.18
2023-12-25 | 2023-12-28 | 0.0 | 0.0 | 0.1 | - | - | No | - | 266.52 | 8.11 | 0.41 | 0.76 | 1.05 | 23.83 | -37.3 | 0.20
2024-01-01 | 2024-01-04 | 0.0 | 0.0 | 0.0 | - | - | No | - | 265.60 | 8.05 | 0.41 | 0.98 | 0.70 | 25.05 | 45.5 | 0.20
2024-01-08 | 2024-01-10 | 0.0 | 0.0 | 0.0 | - | - | No | - | 258.85 | 8.13 | 0.40 | 0.84 | 0.68 | 23.99 | 54.3 | 0.19
2024-01-15 | 2024-01-17 | 0.0 | 0.0 | 0.0 | - | - | No | - | 263.01 | 8.04 | 0.40 | 0.78 | 0.62 | 24.60 | 59.7 | 0.20
2024-02-05 | 2024-02-07 | 0.0 | 0.0 | 0.0 | - | - | No | - | 266.25 | 7.88 | 0.41 | 1.30 | 0.14 | 25.96 | -12.9 | 0.20
2024-03-11 | 2024-03-13 | 0.0 | 0.0 | 0.0 | - | - | No | - | 278.19 | 7.64 | 0.43 | 1.59 | 0.50 | 25.03 | -39.0 | 0.21
2024-03-11 | 2024-04-03 | 0.0 | 0.0 | 0.0 | - | - | No | - | 283.81 | 8.09 | 0.44 | 1.60 | 0.25 | 25.44 | 9.0 | 0.21
2024-03-11 | 2024-05-08 | 0.0 | 0.0 | 0.0 | - | - | No | - | 271.90 | 8.01 | 0.42 | 1.56 | 0.51 | 25.89 | 36.6 | 0.20
2024-03-11 | 2024-05-22 | 0.0 | 0.0 | 0.0 | - | - | No | - | 238.58 | 8.00 | 0.37 | 2.10 | 1.03 | 26.51 | -57.0 | 0.18
2024-03-11 | 2024-06-05 | 0.0 | 0.2 | 0.1 | - | - | No | - | 268.81 | 8.03 | 0.41 | 0.75 | 0.80 | 27.80 | 45.8 | 0.20
2024-03-11 | 2024-06-19 | 0.0 | 0.0 | 0.0 | - | - | No | - | 258.58 | 8.24 | 0.40 | 1.58 | 0.73 | 27.25 | -16.0 | 0.19
2024-03-11 | 2024-07-03 | 0.0 | 0.0 | 0.0 | - | - | No | - | 258.46 | 8.22 | 0.40 | 0.75 | 0.00 | 25.26 | -49.1 | 0.19
2024-03-11 | 2024-07-17 | 0.0 | 0.0 | 0.0 | - | - | No | - | 262.02 | 8.07 | 0.40 | 0.71 | 0.84 | 26.93 | -79.5 | 0.20
2024-03-11 | 2024-08-07 | 0.0 | 0.0 | 0.0 | - | - | No | - | 259.32 | 8.18 | 0.40 | 0.96 | 1.40 | 25.84 | -91.5 | 0.19
2024-03-11 | 2024-08-19 | 0.0 | 0.0 | 0.0 | - | - | No | - | 257.84 | 8.15 | 0.40 | 0.85 | 1.24 | 26.53 | -46.0 | 0.19
2024-03-11 | 2024-09-04 | 0.0 | 0.0 | 0.0 | - | - | No | - | 285.19 | 8.00 | 0.44 | 0.92 | 0.55 | 27.16 | -26.4 | 0.21
2024-03-11 | 2024-09-18 | 0.0 | 0.0 | 0.0 | - | - | No | - | 259.36 | 8.09 | 0.40 | 1.08 | 1.14 | 26.61 | -15.7 | 0.19
2024-03-11 | 2024-10-08 | 0.0 | 0.0 | 0.0 | - | - | No | - | 257.43 | 8.39 | 0.40 | 2.04 | 1.16 | 29.40 | -39.1 | 0.19
2024-03-11 | 2024-10-23 | 0.0 | 0.0 | 0.0 | - | - | No | - | 265.33 | 8.16 | 0.41 | 0.61 | 1.66 | 26.53 | -176.1 | 0.20
2024-03-11 | 2024-11-06 | 0.0 | 0.0 | 0.0 | - | - | No | - | 293.66 | 8.19 | 0.45 | 1.78 | 0.05 | 24.72 | -134.1 | 0.22
2024-03-11 | 2024-11-20 | 0.0 | 0.0 | 0.0 | - | - | No | - | 256.16 | 8.11 | 0.39 | 0.86 | 0.66 | 24.77 | -106.0 | 0.19
2024-03-11 | 2024-12-04 | 0.0 | 0.0 | 0.0 | - | - | No | - | 264.29 | 8.33 | 0.41 | 1.91 | 0.79 | 24.73 | 7.5 | 0.20
2024-03-11 | 2024-12-18 | 0.0 | 0.0 | 0.0 | - | - | No | - | 274.81 | 8.09 | 0.42 | 0.62 | 0.71 | 24.91 | 7.0 | 0.20
| RHMW12A Headspace and Product Gauging | [7 empty] | RHMW12A Parameter Readings
WEEK | DATE | AMBIENT | TOP-OF-CASING HEADSPACE | GROUNDWATER HEADSPACE | TAPE | DTW (Raw) | PRODUCT? | THICKNESS | TDS | pH | Sp. Cond. | D.O. | Turbidity | TEMP | ORP | SAL
|  | (ppmv) | (ppmv) | (ppmv) | (Serial #) | (ft btoc) | (Yes/No) | (ft) | (ppm) |  | (mS/cm) | (mg/L) | (NTU) | (°C) | (Mv) | (psu)
06/05/2023 | 06/06/2023 | 0.0 | 0.0 | - | N-6 | 220.52 | No | - | 210.56 | 8.21 | 0.32 | 5.35 | 0.63 | 25.85 | 82.8 | 0.16
07/03/2023 | 07/07/2023 | 0.0 | 0.0 | - | N-6 | 220.86 | No | - | 210.41 | 8.31 | 0.32 | 5.30 | 0.03 | 25.10 | 176.6 | 0.16
07/31/2023 | 08/03/2023 | 0.0 | 0.0 | - | N-5 | 220.9 | No | - | 217.70 | 8.26 | 0.33 | 5.75 | 0.19 | 25.75 | 173.9 | 0.16
09/04/2023 | 09/07/2023 | 0.0 | 0.0 | - | N-5 | 221.04 | No | - | 219.25 | 8.37 | 0.34 | 6.20 | 0.14 | 25.96 | 100.5 | 0.16
10/02/2023 | 10/03/2023 | 0.0 | 0.0 | - | N-6 | 221.09 | No | - | 209.58 | 8.48 | 0.32 | 6.25 | 0.25 | 25.90 | 176.8 | 0.16
11/06/2023 | 11/09/2023 | 0.0 | 0.0 | - | N-5 | 221.22 | No | - | 201.72 | 8.42 | 0.30 | 6.60 | 0.00 | 25.77 | 226.9 | 0.15
2023-12-04 | 2023-12-07 | 0.0 | 0.0 | - | N-4 | 221.09 | No | - | 208.56 | 8.42 | 0.32 | 6.68 | 0.04 | 25.04 | 222.5 | 0.15
2024-01-01 | 2024-01-05 | 0.0 | 0.0 | - | N-6 | 221.03 | No | - | 222.11 | 8.25 | 0.34 | 6.81 | 0.39 | 25.40 | 185.8 | 0.16
2024-02-12 | 2024-02-12 | 0.0 | 0.0 | - | N-4 | 220.89 | No | - | 194.84 | 8.08 | 0.30 | 6.95 | 0.54 | 24.65 | 224.6 | 0.14
2024-03-18 | 2024-03-18 | 0.0 | 0.0 | - | N-6 | 220.87 | No | - | 199.04 | 8.27 | 0.31 | 6.85 | 0.63 | 24.55 | 226.3 | 0.15
2024-03-18 | 2024-04-08 | 0.0 | 0.0 | - | N-6 | 220.95 | No | - | 198.86 | 8.26 | 0.31 | 6.91 | 0.85 | 25.98 | 192.3 | 0.15
2024-03-18 | 2024-05-14 | 0.0 | 0.0 | - | N-6 | 220.73 | No | - | 210.51 | 8.38 | 0.32 | 7.07 | 0.06 | 25.26 | 250.8 | 0.16
2024-03-18 | 2024-05-29 | 0.0 | 0.0 | - | N-5 | 220.45 | No | - | 195.39 | 8.28 | 0.30 | 7.27 | 0.11 | 25.25 | 229.8 | 0.14
2024-03-18 | 2024-06-11 | 0.0 | 0.0 | - | N-5 | 220.51 | No | - | 215.08 | 8.39 | 0.33 | 7.01 | 0.06 | 25.39 | 247.9 | 0.16
2024-03-18 | 2024-06-25 | 0.0 | 0.0 | - | N-6 | 220.52 | No | - | 189.08 | 8.56 | 0.29 | 7.11 | 0.05 | 25.15 | 213.3 | 0.14
2024-03-18 | 2024-07-12 | 0.0 | 0.0 | - | N-5 | 220.45 | No | - | 190.45 | 8.47 | 0.29 | 7.33 | 0.02 | 25.23 | 181.3 | 0.14
2024-03-18 | 2024-07-26 | 0.0 | 0.0 | - | N-5 | 220.48 | No | - | 237.29 | 8.49 | 0.37 | 7.21 | 0.00 | 24.98 | 214.9 | 0.18
2024-03-18 | 2024-08-15 | 0.0 | 0.0 | - | N-5 | 220.47 | No | - | 191.10 | 8.41 | 0.29 | 7.21 | 0.25 | 25.66 | 181.0 | 0.14
2024-03-18 | 2024-08-30 | 0.0 | 0.0 | - | N-5 | 220.43 | No | - | 215.49 | 8.47 | 0.33 | 7.22 | 0.00 | 25.46 | 290.4 | 0.16
2024-03-18 | 2024-09-13 | 0.0 | 0.0 | - | 252094 | 220.37 | No | - | 195.50 | 8.48 | 0.30 | 7.18 | 0.13 | 26.36 | 216.5 | 0.14
2024-03-18 | 2024-09-27 | 0.0 | 0.0 | - | N-5 | 220.37 | No | - | 185.94 | 8.48 | 0.29 | 7.24 | 0.21 | 25.64 | 125.5 | 0.14
2024-03-18 | 2024-10-18 | 0.0 | 0.0 | - | N-3 | 220.33 | No | - | 211.20 | 8.38 | 0.32 | 7.27 | 0.19 | 26.51 | 156.0 | 0.16
2024-03-18 | 2024-10-31 | 0.0 | 0.0 | - | N-4 | 220.36 | No | - | 188.95 | 8.56 | 0.29 | 7.28 | 0.00 | 25.15 | 19.5 | 0.14
2024-03-18 | 2024-11-15 | 0.0 | 0.0 | - | N-3 | 220.21 | No | - | 190.36 | 8.48 | 0.29 | 7.32 | 0.00 | 25.00 | 74.3 | 0.14
2024-03-18 | 2024-11-26 | 0.0 | 0.0 | - | N-4 | 220.28 | No | - | 208.45 | 8.44 | 0.32 | 7.29 | 0.49 | 25.47 | 182.3 | 0.15
2024-03-18 | 2024-12-13 | 0.0 | 0.0 | - | N-5 | 220.28 | No | - | 197.31 | 8.39 | 0.30 | 7.36 | 0.16 | 25.46 | 157.1 | 0.15
2024-03-18 | 2024-12-27 | 0.0 | 0.0 | - | N-5 | 220.26 | No | - | 202.97 | 8.34 | 0.31 | 7.44 | 0.27 | 25.10 | 197.4 | 0.15
| RHMW13-04 Headspace and Product Gauging | [7 empty] | RHMW13-04 Parameter Readings
WEEK | DATE | AMBIENT | TOP-OF-CASING HEADSPACE | GROUNDWATER HEADSPACE | TAPE | DTW (Raw) | PRODUCT? | THICKNESS | TDS | pH | Sp. Cond. | D.O. | Turbidity | TEMP | ORP | SAL
|  | (ppmv) | (ppmv) | (ppmv) | (Serial #) | (ft btoc) | (Yes/No) | (ft) | (ppm) |  | (mS/cm) | (mg/L) | (NTU) | (°C) | (Mv) | (psu)
10/23/2023 | 10/25/2023 | 0.0 | 0.0 | 0.0 | - | - | No | - | 214.49 | 8.03 | 0.33 | 1.54 | 0.32 | 23.89 | 205.2 | 0.16
2023-11-20 | 2023-11-20 | 0.0 | 0.0 | 0.0 | - | - | No | - | 224.54 | 8.20 | 0.35 | 1.09 | 0.00 | 23.58 | 178.7 | 0.17
2023-11-27 | 2023-11-28 | 0.0 | 0.0 | 0.0 | - | - | No | - | 208.90 | 8.17 | 0.32 | 0.84 | 0.26 | 23.23 | 196.1 | 0.15
2023-12-04 | 2023-12-07 | 0.0 | 0.0 | 0.0 | - | - | No | - | 206.18 | 7.90 | 0.32 | 2.77 | 0.00 | 23.06 | 182.0 | 0.15
2023-12-11 | 2023-12-12 | 0.0 | 0.0 | 0.0 | - | - | No | - | 213.52 | 7.96 | 0.33 | 2.43 | 0.00 | 22.60 | 202.0 | 0.16
2023-12-18 | 2023-12-19 | 0.0 | 0.0 | 0.0 | - | - | No | - | 201.99 | 8.00 | 0.31 | 2.07 | 0.00 | 22.33 | 199.1 | 0.15
2023-12-25 | 2023-12-27 | 0.0 | 0.0 | 0.0 | - | - | No | - | 215.77 | 8.09 | 0.33 | 2.21 | 0.00 | 23.66 | 172.8 | 0.16
2024-01-01 | 2024-01-03 | 0.0 | 0.0 | 0.0 | - | - | No | - | 221.94 | 7.94 | 0.34 | 1.78 | 0.23 | 22.79 | 221.7 | 0.16
2024-01-08 | 2024-01-08 | 0.0 | 0.0 | 0.0 | - | - | No | - | 208.35 | 7.86 | 0.32 | 1.79 | 0.00 | 22.36 | 188.3 | 0.15
2024-01-15 | 2024-01-16 | 0.0 | 0.0 | 0.0 | - | - | No | - | 222.22 | 7.93 | 0.34 | 1.78 | 0.31 | 22.86 | 224.0 | 0.16
2024-02-12 | 2024-02-16 | 0.0 | 0.0 | 0.0 | - | - | No | - | 193.77 | 7.82 | 0.30 | 2.37 | 0.66 | 21.73 | 195.0 | 0.14
2024-03-18 | 2024-03-18 | 0.0 | 0.0 | 0.0 | - | - | No | - | 227.79 | 8.07 | 0.35 | 1.35 | 0.25 | 22.88 | 148.5 | 0.17
2024-03-18 | 2024-04-08 | 0.0 | 0.0 | 0.0 | - | - | No | - | 230.10 | 7.74 | 0.35 | 4.27 | 0.00 | 24.80 | 207.2 | 0.17
2024-03-18 | 2024-05-13 | 0.0 | 0.0 | 0.0 | - | - | No | - | 204.69 | 7.46 | 0.31 | 3.90 | 0.71 | 24.93 | 227.4 | 0.15
2024-03-18 | 2024-05-29 | 0.0 | 0.0 | 0.0 | - | - | No | - | 223.96 | 7.77 | 0.34 | 2.75 | 8.91 | 26.08 | 243.1 | 0.17
2024-03-18 | 2024-06-10 | 0.0 | 0.0 | 0.0 | - | - | No | - | 214.60 | 7.92 | 0.33 | 4.66 | 0.70 | 27.73 | 174.4 | 0.16
2024-03-18 | 2024-06-24 | 0.0 | 0.0 | 0.0 | - | - | No | - | 204.65 | 8.21 | 0.31 | 2.27 | 0.22 | 25.21 | 185.0 | 0.15
2024-03-18 | 2024-07-08 | 0.0 | 0.0 | 0.0 | - | - | No | - | 237.73 | 7.95 | 0.37 | 1.74 | 0.29 | 24.52 | 192.7 | 0.18
2024-03-18 | 2024-07-22 | 0.0 | 0.0 | 0.0 | - | - | No | - | 205.54 | 7.90 | 0.32 | 2.85 | 0.87 | 27.76 | 176.0 | 0.15
2024-03-18 | 2024-08-12 | 0.0 | 0.0 | 0.0 | - | - | No | - | 201.75 | 7.68 | 0.31 | 3.35 | 0.30 | 24.39 | 225.0 | 0.15
2024-03-18 | 2024-08-26 | 0.0 | 0.0 | 0.0 | - | - | No | - | 243.64 | 8.04 | 0.37 | 1.84 | 0.31 | 25.33 | 142.0 | 0.18
2024-03-18 | 2024-09-10 | 0.0 | 0.0 | 0.0 | - | - | No | - | 210.23 | 7.88 | 0.32 | 1.91 | 0.69 | 28.31 | 195.8 | 0.16
2024-03-18 | 2024-09-23 | 0.0 | 0.0 | 0.0 | - | - | No | - | 165.93 | 8.01 | 0.26 | 2.62 | 0.91 | 26.67 | 161.9 | 0.12
2024-03-18 | 2024-10-14 | 0.0 | 0.0 | 0.0 | - | - | No | - | 209.55 | 7.96 | 0.32 | 2.67 | 0.65 | 24.51 | 224.9 | 0.16
2024-03-18 | 2024-10-28 | 0.0 | 0.0 | 0.0 | - | - | No | - | 207.70 | 7.89 | 0.32 | 2.07 | 0.25 | 23.35 | 57.2 | 0.15
2024-03-18 | 2024-11-12 | 0.0 | 0.0 | 0.0 | - | - | No | - | 224.34 | 7.99 | 0.35 | 2.38 | 0.00 | 23.27 | 142.3 | 0.17
2024-03-18 | 2024-11-22 | 0.0 | 0.0 | 0.0 | - | - | No | - | 219.42 | 7.94 | 0.34 | 1.72 | 0.35 | 23.00 | 63.6 | 0.16
2024-03-18 | 2024-12-09 | 0.0 | 0.0 | 0.0 | - | - | No | - | 210.66 | 7.95 | 0.32 | 1.94 | 0.09 | 22.86 | 134.3 | 0.16
2024-03-18 | 2024-12-20 | 0.0 | 0.0 | 0.0 | - | - | No | - | 220.01 | 7.96 | 0.34 | 2.81 | 0.22 | 23.64 | 163.1 | 0.16
| RHMW13-05 Headspace and Product Gauging | [7 empty] | RHMW13-05 Parameter Readings
WEEK | DATE | AMBIENT | TOP-OF-CASING HEADSPACE | GROUNDWATER HEADSPACE | TAPE | DTW (Raw) | PRODUCT? | THICKNESS | TDS | pH | Sp. Cond. | D.O. | Turbidity | TEMP | ORP | SAL
|  | (ppmv) | (ppmv) | (ppmv) | (Serial #) | (ft btoc) | (Yes/No) | (ft) | (ppm) |  | (mS/cm) | (mg/L) | (NTU) | (°C) | (Mv) | (psu)
06/05/2023 | 06/06/2023 | 0.0 | 0.0 | 0.0 | - | - | No | - | 251.19 | 8.03 | 0.39 | 1.07 | 1.37 | 26.79 | 140.8 | 0.19
07/03/2023 | 07/05/2023 | 0.0 | 0.0 | 0.0 | - | - | No | - | 222.65 | 7.77 | 0.34 | 0.44 | 8.11 | 26.03 | 121.2 | 0.17
07/31/2023 | 08/01/2023 | 0.0 | 0.0 | 0.0 | - | - | No | - | 236.74 | 7.64 | 0.36 | 0.75 | 5.92 | 28.57 | 10.4 | 0.18
09/04/2023 | 09/05/2023 | 0.0 | 0.0 | 0.0 | - | - | No | - | 234.22 | 7.59 | 0.36 | 1.39 | 2.25 | 31.51 | -26.7 | 0.17
10/02/2023 | 10/05/2023 | 0.0 | 0.0 | 0.0 | - | - | No | - | 242.57 | 7.72 | 0.37 | 3.88 | 1.66 | 27.05 | 158.6 | 0.18
10/30/2023 | 10/31/2023 | 0.0 | 0.0 | 0.0 | - | - | No | - | 218.57 | 8.02 | 0.34 | 2.35 | 1.46 | 24.30 | 197.3 | 0.16
11/06/2023 | 11/09/2023 | 0.0 | 0.0 | 0.0 | - | - | No | - | 216.85 | 7.78 | 0.30 | 3.70 | 0.14 | 23.41 | 202.8 | 0.16
2023-11-13 | 2023-11-14 | 0.0 | 0.0 | 0.0 | - | - | No | - | 221.25 | 7.89 | 0.34 | 2.71 | 0.36 | 22.51 | 92.6 | 0.16
| RHMW14-03 Headspace and Product Gauging | [7 empty] | RHMW14-03 Parameter Readings
WEEK | DATE | AMBIENT | TOP-OF-CASING HEADSPACE | GROUNDWATER HEADSPACE | TAPE | DTW (Raw) | PRODUCT? | THICKNESS | TDS | pH | Sp. Cond. | D.O. | Turbidity | TEMP | ORP | SAL
|  | (ppmv) | (ppmv) | (ppmv) | (Serial #) | (ft btoc) | (Yes/No) | (ft) | (ppm) |  | (mS/cm) | (mg/L) | (NTU) | (°C) | (Mv) | (psu)
06/05/2023 | 06/07/2023 | 0.0 | 0.0 | 0.0 | - | - | No | - | 208.59 | 7.78 | 0.32 | 1.09 | 3.71 | 25.10 | 185.4 | 0.15
07/03/2023 | 07/07/2023 | 0.0 | 0.0 | 0.0 | - | - | No | - | 188.24 | 7.95 | 0.29 | 1.92 | 0.59 | 25.79 | 190.3 | 0.14
07/31/2023 | 08/04/2023 | 0.0 | 0.0 | 0.0 | - | - | No | - | 192.57 | 7.33 | 0.30 | 1.92 | 0.00 | 28.66 | 115.2 | 0.14
09/04/2023 | 09/06/2023 | 0.0 | 0.0 | 0.0 | - | - | No | - | 193.57 | 7.76 | 0.30 | 3.10 | 0.37 | 26.87 | 110.5 | 0.14
10/02/2023 | 10/02/2023 | 0.0 | 0.0 | 0.0 | - | - | No | - | 185.16 | 7.97 | 0.28 | 2.09 | 1.39 | 27.37 | 45.9 | 0.14
10/23/2023 | 10/24/2023 | 0.0 | 0.0 | 0.0 | - | - | No | - | 184.21 | 7.99 | 0.28 | 2.56 | 0.28 | 25.15 | 222.9 | 0.14
10/30/2023 | 10/30/2023 | 0.0 | 0.0 | 0.0 | - | - | No | - | 187.06 | 8.05 | 0.29 | 1.96 | 0.83 | 25.36 | 212.4 | 0.14
11/06/2023 | 11/06/2023 | 0.0 | 0.0 | 0.0 | - | - | No | - | 179.23 | 7.94 | 0.30 | 3.50 | 0.31 | 26.75 | 221.9 | 0.13
2023-11-13 | 2023-11-15 | 0.0 | 0.0 | 0.0 | - | - | No | - | 185.14 | 7.95 | 0.28 | 1.64 | 0.29 | 23.89 | 224.6 | 0.14
2023-11-20 | 2023-11-22 | 0.0 | 0.0 | 0.0 | - | - | No | - | 172.93 | 7.95 | 0.27 | 1.59 | 0.16 | 23.99 | 165.4 | 0.13
2023-11-27 | 2023-11-27 | 0.0 | 0.0 | 0.0 | - | - | No | - | 184.27 | 7.89 | 0.28 | 2.78 | 2.57 | 25.40 | 243.9 | 0.14
2023-12-04 | 2023-12-04 | 0.0 | 0.0 | 0.0 | - | - | No | - | 180.81 | 7.94 | 0.28 | 2.12 | 0.47 | 23.78 | 183.2 | 0.13
2023-12-11 | 2023-12-13 | 0.0 | 0.0 | 0.0 | - | - | No | - | 187.99 | 7.83 | 0.29 | 2.63 | 1.06 | 23.87 | 230.4 | 0.14
2023-12-18 | 2023-12-20 | 0.0 | 0.0 | 1.5 | - | - | No | - | 171.41 | 8.07 | 0.26 | 1.35 | 0.00 | 22.06 | 182.3 | 0.13
2023-12-25 | 2023-12-28 | 0.0 | 0.0 | 0.0 | - | - | No | - | 184.91 | 7.94 | 0.28 | 2.93 | 0.89 | 24.27 | 184.9 | 0.14
2024-01-01 | 2024-01-04 | 0.0 | 0.0 | 20.2 | - | - | No | - | 187.21 | 7.93 | 0.29 | 3.52 | 0.48 | 25.69 | 195.5 | 0.14
2024-01-08 | 2024-01-10 | 0.0 | 0.0 | 0.0 | - | - | No | - | 183.97 | 7.93 | 0.28 | 1.43 | 0.64 | 24.36 | 196.5 | 0.14
2024-01-15 | 2024-01-17 | 0.0 | 0.0 | 0.0 | - | - | No | - | 183.19 | 7.89 | 0.28 | 1.58 | 0.65 | 23.93 | 233.4 | 0.14
2024-02-05 | 2024-02-07 | 0.0 | 0.0 | 0.0 | - | - | No | - | 195.62 | 7.60 | 0.30 | 2.62 | 0.14 | 26.29 | 127.5 | 0.14
2024-03-11 | 2024-03-13 | 0.0 | 0.0 | 0.0 | - | - | No | - | 195.54 | 7.84 | 0.30 | 2.03 | 0.33 | 23.19 | 175.0 | 0.14
2024-03-11 | 2024-04-03 | 0.0 | 0.0 | 0.0 | - | - | No | - | 199.20 | 7.85 | 0.31 | 2.78 | 0.14 | 24.92 | 209.0 | 0.15
2024-03-11 | 2024-05-08 | 0.0 | 0.0 | 0.0 | - | - | No | - | 190.77 | 7.90 | 0.29 | 3.02 | 0.52 | 25.67 | 208.2 | 0.14
2024-03-11 | 2024-05-22 | 0.0 | 0.0 | 0.0 | - | - | No | - | 166.20 | 8.04 | 0.26 | 2.67 | 1.05 | 25.62 | 181.9 | 0.12
2024-03-11 | 2024-06-05 | 0.0 | 0.0 | 0.0 | - | - | No | - | 194.35 | 7.85 | 0.30 | 1.87 | 0.66 | 26.94 | 204.6 | 0.14
2024-03-11 | 2024-06-19 | 0.0 | 0.0 | 0.0 | - | - | No | - | 179.83 | 8.10 | 0.28 | 4.39 | 0.36 | 25.42 | 187.7 | 0.13
2024-03-11 | 2024-07-03 | 0.0 | 0.0 | 0.0 | - | - | No | - | 178.90 | 8.02 | 0.28 | 1.54 | 0.00 | 24.05 | 214.7 | 0.13
2024-03-11 | 2024-07-17 | 0.0 | 0.0 | 0.0 | - | - | No | - | 183.11 | 8.08 | 0.28 | 2.34 | 0.23 | 25.41 | 180.8 | 0.14
2024-03-11 | 2024-08-07 | 0.0 | 0.0 | 0.0 | - | - | No | - | 181.84 | 8.03 | 0.28 | 1.03 | 1.54 | 26.96 | 184.3 | 0.13
2024-03-11 | 2024-08-19 | 0.0 | 0.0 | 0.0 | - | - | No | - | 184.27 | 7.80 | 0.28 | 2.58 | 1.02 | 28.18 | 174.5 | 0.14
2024-03-11 | 2024-09-04 | 0.0 | 0.0 | 0.0 | - | - | No | - | 206.80 | 7.75 | 0.32 | 2.50 | 3.80 | 29.12 | 193.2 | 0.15
2024-03-11 | 2024-09-18 | 0.0 | 0.0 | 0.0 | - | - | No | - | 181.85 | 8.06 | 0.28 | 0.66 | 1.08 | 27.00 | 182.0 | 0.13
2024-03-11 | 2024-10-08 | 0.0 | 0.0 | 0.0 | - | - | No | - | 180.26 | 8.09 | 0.28 | 2.41 | 0.83 | 28.33 | 77.8 | 0.13
2024-03-11 | 2024-10-23 | 0.0 | 0.0 | 0.0 | - | - | No | - | 185.04 | 7.95 | 0.28 | 1.90 | 1.45 | 25.90 | 94.0 | 0.14
2024-03-11 | 2024-11-06 | 0.0 | 0.0 | 0.0 | - | - | No | - | 203.93 | 8.07 | 0.31 | 2.70 | 0.20 | 24.47 | 70.9 | 0.15
2024-03-11 | 2024-11-20 | 0.0 | 0.0 | 0.0 | - | - | No | - | 182.04 | 7.98 | 0.28 | 1.91 | 0.51 | 24.58 | 148.4 | 0.13
2024-03-11 | 2024-12-04 | 0.0 | 0.0 | 0.0 | - | - | No | - | 193.27 | 7.90 | 0.30 | 1.89 | 0.58 | 25.02 | 157.9 | 0.14
2024-03-11 | 2024-12-18 | 0.0 | 0.0 | 0.0 | - | - | No | - | 193.48 | 7.87 | 0.30 | 1.85 | 0.83 | 25.60 | 181.1 | 0.14
| RHMW15-05 Headspace and Product Gauging | [7 empty] | RHMW15-05 Parameter Readings
WEEK | DATE | AMBIENT | TOP-OF-CASING HEADSPACE | GROUNDWATER HEADSPACE | TAPE | DTW (Raw) | PRODUCT? | THICKNESS | TDS | pH | Sp. Cond. | D.O. | Turbidity | TEMP | ORP | SAL
|  | (ppmv) | (ppmv) | (ppmv) | (Serial #) | (ft btoc) | (Yes/No) | (ft) | (ppm) |  | (mS/cm) | (mg/L) | (NTU) | (°C) | (Mv) | (psu)
06/05/2023 | 06/05/2023 | 0.0 | 0.0 | 0.0 | - | - | No | - | 220.34 | 7.84 | 0.34 | 1.34 | 0.95 | 25.35 | 208.1 | 0.16
07/03/2023 | 07/03/2023 | 0.0 | 0.0 | 0.0 | - | - | No | - | 205.82 | 7.82 | 0.32 | 1.90 | 0.79 | 28.15 | 167.0 | 0.15
07/31/2023 | 08/03/2023 | 0.0 | 0.0 | 0.0 | - | - | No | - | 217.33 | 7.86 | 0.33 | 1.17 | 0.07 | 29.51 | 82.7 | 0.16
09/04/2023 | 09/07/2023 | 0.0 | 0.0 | 0.0 | - | - | No | - | 215.79 | 7.77 | 0.33 | 2.34 | 0.00 | 28.21 | 104.8 | 0.16
10/02/2023 | 10/04/2023 | 0.0 | 0.0 | 0.0 | - | - | No | - | 215.68 | 7.96 | 0.33 | 2.70 | 0.68 | 27.46 | 128.7 | 0.16
10/23/2023 | 10/23/2023 | 0.0 | 0.0 | 0.1 | - | - | No | - | 214.25 | 7.80 | 0.33 | 1.39 | 0.30 | 27.04 | 197.1 | 0.16
10/30/2023 | 11/01/2023 | 0.0 | 0.0 | 0.0 | - | - | No | - | 212.35 | 7.95 | 0.33 | 1.91 | 1.27 | 25.24 | 198.4 | 0.16
11/06/2023 | 11/08/2023 | 0.0 | 0.0 | 0.0 | - | - | No | - | 201.21 | 7.78 | 0.30 | 2.00 | 0.04 | 25.09 | 193.4 | 0.15
2023-11-13 | 2023-11-13 | 0.0 | 0.0 | 0.0 | - | - | No | - | 207.99 | 7.55 | 0.32 | 2.19 | 0.18 | 25.49 | 217.3 | 0.15
2023-11-20 | 2023-11-21 | 0.0 | 0.0 | 0.0 | - | - | No | - | 202.29 | 8.00 | 0.31 | 1.47 | 0.43 | 26.68 | 215.2 | 0.15
2023-11-27 | 2023-11-29 | 0.0 | 0.0 | 0.0 | - | - | No | - | 203.91 | 8.01 | 0.31 | 1.54 | 0.02 | 22.47 | 194.2 | 0.15
2023-12-04 | 2023-12-06 | 0.0 | 0.0 | 0.0 | - | - | No | - | 202.10 | 7.89 | 0.31 | 1.22 | 0.49 | 24.69 | 204.9 | 0.15
2023-12-11 | 2023-12-11 | 0.0 | 0.0 | 0.0 | - | - | No | - | 209.78 | 7.96 | 0.32 | 1.47 | 0.27 | 24.84 | 154.4 | 0.16
2023-12-18 | 2023-12-18 | 0.0 | 0.0 | 0.0 | - | - | No | - | 208.20 | 7.91 | 0.32 | 1.71 | 0.28 | 22.29 | 204.1 | 0.15
2023-12-25 | 2023-12-29 | 0.0 | 0.0 | 0.0 | - | - | No | - | 202.75 | 7.59 | 0.31 | 2.78 | 0.76 | 22.69 | 229.9 | 0.15
2024-01-01 | 2024-01-05 | 0.0 | 0.0 | 0.0 | - | - | No | - | 206.76 | 8.02 | 0.32 | 1.25 | 0.53 | 24.33 | 218.7 | 0.15
2024-01-08 | 2024-01-08 | 0.0 | 0.0 | 0.0 | - | - | No | - | 208.35 | 7.86 | 0.32 | 1.79 | 0.00 | 22.36 | 188.3 | 0.15
2024-01-15 | 2024-01-15 | 0.0 | 0.0 | 0.0 | - | - | No | - | 202.85 | 7.57 | 0.31 | 2.84 | 1.86 | 23.30 | 198.6 | 0.15
2024-02-05 | 2024-02-05 | 0.0 | 0.0 | 0.3 | - | - | No | - | 202.48 | 7.91 | 0.31 | 1.80 | 0.44 | 24.31 | 146.9 | 0.15
2024-03-11 | 2024-03-11 | 0.0 | 0.0 | 0.0 | - | - | No | - | 224.36 | 7.84 | 0.35 | 2.25 | 0.16 | 23.40 | 196.3 | 0.17
2024-03-11 | 2024-04-01 | 0.0 | 0.0 | 0.0 | - | - | No | - | 215.48 | 7.79 | 0.33 | 1.92 | 0.69 | 28.67 | 185.3 | 0.16
2024-03-11 | 2024-05-06 | 0.0 | 0.0 | 0.0 | - | - | No | - | 215.78 | 7.69 | 0.33 | 2.79 | 0.31 | 25.61 | 201.5 | 0.16
2024-03-11 | 2024-05-20 | 0.0 | 0.0 | 0.0 | - | - | No | - | 215.44 | 7.88 | 0.33 | 2.22 | 0.67 | 28.11 | 222.4 | 0.16
2024-03-11 | 2024-06-03 | 0.0 | 0.0 | 0.0 | - | - | No | - | 224.40 | 7.73 | 0.35 | 2.75 | 0.13 | 29.67 | 220.4 | 0.17
2024-03-11 | 2024-06-17 | 0.0 | 0.0 | 0.0 | - | - | No | - | 198.71 | 7.81 | 0.31 | 4.12 | 0.40 | 27.43 | 37.4 | 0.15
2024-03-11 | 2024-07-01 | 0.0 | 0.0 | 0.0 | - | - | No | - | 201.73 | 7.70 | 0.31 | 4.06 | 0.79 | 29.90 | 201.4 | 0.15
2024-03-11 | 2024-07-15 | 0.0 | 0.0 | 0.0 | - | - | No | - | 212.36 | 7.78 | 0.33 | 1.98 | 1.91 | 30.76 | 165.0 | 0.16
2024-03-11 | 2024-08-05 | 0.0 | 0.0 | 0.0 | - | - | No | - | 227.46 | 7.78 | 0.35 | 2.06 | 1.39 | 29.69 | 210.6 | 0.17
2024-03-11 | 2024-08-21 | 0.0 | 0.0 | 0.0 | - | - | No | - | 210.15 | 7.33 | 0.32 | 2.26 | 1.31 | 29.47 | 181.2 | 0.16
2024-03-11 | 2024-09-05 | 0.0 | 0.0 | 0.0 | - | - | No | - | 220.73 | 7.90 | 0.34 | 1.79 | 1.21 | 30.35 | 210.1 | 0.16
2024-03-11 | 2024-09-16 | 0.0 | 0.0 | 0.0 | - | - | No | - | 208.20 | 7.88 | 0.32 | 1.39 | 0.84 | 28.74 | 209.1 | 0.15
2024-03-11 | 2024-10-07 | 0.0 | 0.0 | 0.0 | - | - | No | - | 188.81 | 7.54 | 0.29 | 2.92 | 1.32 | 28.10 | 155.2 | 0.14
2024-03-11 | 2024-10-21 | 0.0 | 0.0 | 0.0 | - | - | No | - | 212.28 | 7.74 | 0.33 | 2.24 | 2.22 | 30.72 | 89.2 | 0.16
2024-03-11 | 2024-11-05 | 0.0 | 0.0 | 0.0 | - | - | No | - | 225.25 | 7.90 | 0.35 | 2.20 | 1.17 | 25.97 | 91.0 | 0.17
2024-03-11 | 2024-11-18 | 0.0 | 0.0 | 0.0 | - | - | No | - | 198.93 | 7.99 | 0.31 | 2.76 | 0.00 | 24.76 | 94.8 | 0.15
2024-03-11 | 2024-12-02 | 0.0 | 0.0 | 0.0 | - | - | No | - | 219.73 | 7.88 | 0.34 | 2.14 | 0.97 | 25.19 | 141.1 | 0.16
2024-03-11 | 2024-12-16 | 0.0 | 0.0 | 0.0 | - | - | No | - | 204.61 | 7.93 | 0.31 | 1.46 | 0.37 | 25.22 | 234.4 | 0.15
| RHMW16 Headspace and Product Gauging | [7 empty] | RHMW16 Parameter Readings
WEEK | DATE | AMBIENT | TOP-OF-CASING HEADSPACE | GROUNDWATER HEADSPACE | TAPE | DTW (Raw) | PRODUCT? | THICKNESS | TDS | pH | Sp. Cond. | D.O. | Turbidity | TEMP | ORP | SAL
|  | (ppmv) | (ppmv) | (ppmv) | (Serial #) | (ft btoc) | (Yes/No) | (ft) | (ppm) |  | (mS/cm) | (mg/L) | (NTU) | (°C) | (Mv) | (psu)
06/05/2023 | 06/05/2023 | 0.0 | 0.1 | - | N-6 | 201.71 | No | - | 246.45 | 7.85 | 0.38 | 8.86 | 0.65 | 25.56 | 207.8 | 0.18
07/03/2023 | 07/07/2023 | 0.0 | 0.0 | - | N-6 | 202.06 | No | - | 242.73 | 7.91 | 0.37 | 8.30 | 0.17 | 25.29 | 196.5 | 0.18
07/31/2023 | 08/03/2023 | 0.0 | 0.0 | - | N-5 | 202.12 | No | - | 249.02 | 7.69 | 0.38 | 8.28 | 3.05 | 25.47 | 134.6 | 0.19
09/04/2023 | 09/07/2023 | 0.0 | 0.0 | - | N-6 | 202.25 | No | - | 251.53 | 7.86 | 0.39 | 8.66 | 1.77 | 25.93 | 127.5 | 0.19
10/02/2023 | 10/05/2023 | 0.0 | 0.0 | - | N-3 | 202.29 | No | - | 253.70 | 7.88 | 0.39 | 8.49 | 0.45 | 26.43 | 287.3 | 0.19
10/23/2023 | 10/26/2023 | 0.0 | 0.1 | - | N-4 | 202.47 | No | - | 240.26 | 8.05 | 0.37 | 8.55 | 0.11 | 25.01 | 210.8 | 0.18
10/30/2023 | 10/31/2023 | 0.0 | 0.1 | - | N-6 | 202.39 | No | - | 240.29 | 8.02 | 0.37 | 8.56 | 0.00 | 25.69 | 251.5 | 0.18
11/06/2023 | 11/06/2023 | 0.0 | 0.0 | - | N-4 | 202.48 | No | - | 237.74 | 8.05 | 0.40 | 8.70 | 0.23 | 25.05 | 209.7 | 0.18
2023-11-13 | 2023-11-13 | 0.0 | 0.0 | - | N-6 | 202.45 | No | - | 240.91 | 8.04 | 0.37 | 8.92 | 0.00 | 25.56 | 264.1 | 0.18
2023-11-20 | 2023-11-20 | 0.0 | 0.0 | - | N-5 | 202.39 | No | - | 240.77 | 8.02 | 0.37 | 8.60 | 0.21 | 24.74 | 259.2 | 0.18
2023-11-27 | 2023-11-28 | 0.0 | 0.0 | - | N-6 | 202.41 | No | - | 230.84 | 8.00 | 0.36 | 8.50 | 0.00 | 24.16 | 237.7 | 0.17
2023-12-04 | 2023-12-04 | 0.0 | 0.0 | - | N-5 | 202.32 | No | - | 238.72 | 8.07 | 0.37 | 8.55 | 0.15 | 24.32 | 238.1 | 0.18
2023-12-11 | 2023-12-11 | 0.0 | 0.0 | - | N-5 | 202.28 | No | - | 236.23 | 8.06 | 0.36 | 8.57 | 0.04 | 24.57 | 244.9 | 0.18
2023-12-18 | 2023-12-18 | 0.0 | 0.0 | - | N-5 | 202.3 | No | - | 236.66 | 8.00 | 0.36 | 8.54 | 0.37 | 23.93 | 199.7 | 0.18
2023-12-25 | 2023-12-26 | 0.0 | 0.0 | - | N-6 | 202.24 | No | - | 242.72 | 7.97 | 0.37 | 9.21 | 0.42 | 24.84 | 235.5 | 0.18
2024-01-01 | 2024-01-03 | 0.0 | 0.0 | - | N-3 | 202.2 | No | - | 242.71 | 8.04 | 0.37 | 8.65 | 0.00 | 24.33 | 242.7 | 0.18
2024-01-08 | 2024-01-08 | 0.0 | 0.0 | - | N-3 | 202.14 | No | - | 233.46 | 8.01 | 0.36 | 9.10 | 0.00 | 24.25 | 117.9 | 0.17
2024-01-15 | 2024-01-15 | 0.0 | 0.1 | - | N-5 | 202.09 | No | - | 244.55 | 7.95 | 0.38 | 8.58 | 2.13 | 24.86 | 239.2 | 0.18
2024-02-05 | 2024-02-05 | 0.0 | 0.0 | - | N-6 | 202.13 | No | - | 250.66 | 8.05 | 0.39 | 8.48 | 0.12 | 23.91 | 233.0 | 0.19
2024-03-11 | 2024-03-11 | 0.0 | 0.0 | - | N-6 | 202.1 | No | - | 236.00 | 7.92 | 0.36 | 8.67 | 0.32 | 24.41 | 218.6 | 0.18
2024-03-11 | 2024-04-01 | 0.0 | 0.0 | - | N-6 | 202.11 | No | - | 222.83 | 8.01 | 0.34 | 8.67 | 0.22 | 25.28 | 216.8 | 0.17
2024-03-11 | 2024-05-06 | 0.0 | 0.0 | - | N-5 | 201.93 | No | - | 227.01 | 7.94 | 0.35 | 8.61 | 0.32 | 25.15 | 199.6 | 0.17
2024-03-11 | 2024-05-20 | 0.0 | 0.0 | - | N-3 | 201.7 | No | - | 231.91 | 8.06 | 0.36 | 8.43 | 0.05 | 25.81 | 287.3 | 0.17
2024-03-11 | 2024-06-06 | 0.0 | 0.0 | - | N-4 | 201.75 | No | - | 235.69 | 7.86 | 0.36 | 8.68 | 0.16 | 25.32 | 228.1 | 0.18
2024-03-11 | 2024-06-20 | 0.0 | 0.0 | - | N-3 | 201.79 | No | - | 226.65 | 7.93 | 0.35 | 8.80 | 0.79 | 24.87 | 271.1 | 0.17
2024-03-11 | 2024-07-02 | 0.0 | 0.0 | - | N-4 | 201.85 | No | - | 258.09 | 8.02 | 0.40 | 8.61 | 0.00 | 24.76 | 284.7 | 0.19
2024-03-11 | 2024-07-18 | 0.0 | 0.0 | - | N-3 | 201.71 | No | - | 257.93 | 7.98 | 0.40 | 8.51 | 1.93 | 25.88 | 247.6 | 0.19
2024-03-11 | 2024-08-08 | 0.0 | 0.0 | - | N-5 | 201.69 | No | - | 233.09 | 7.98 | 0.36 | 9.13 | 1.25 | 25.63 | 212.5 | 0.17
2024-03-11 | 2024-08-20 | 0.0 | 0.0 | - | N-3 | 201.78 | No | - | 249.44 | 7.95 | 0.38 | 8.71 | 0.00 | 25.43 | 330.9 | 0.19
2024-03-11 | 2024-09-03 | 0.0 | 0.0 | - | N-3 | 201.54 | No | - | 232.22 | 8.03 | 0.36 | 9.21 | 0.29 | 25.63 | 232.6 | 0.17
2024-03-11 | 2024-09-19 | 0.0 | 0.0 | - | 288404 | 201.57 | No | - | 248.50 | 7.97 | 0.38 | 8.58 | 1.54 | 25.54 | 277.0 | 0.18
2024-03-11 | 2024-10-10 | 0.0 | 0.0 | - | N-5 | 201.48 | No | - | 251.65 | 8.03 | 0.39 | 8.74 | 0.00 | 24.94 | 215.4 | 0.19
2024-03-11 | 2024-10-24 | 0.0 | 0.0 | - | N-7 | 201.59 | No | - | 240.13 | 8.01 | 0.37 | 8.58 | 0.14 | 24.68 | 167.3 | 0.18
2024-03-11 | 2024-11-07 | 0.0 | 0.0 | - | N-4 | 201.52 | No | - | 227.41 | 8.05 | 0.35 | 8.54 | 0.01 | 24.50 | 97.4 | 0.17
2024-03-11 | 2024-11-20 | 0.0 | 0.0 | - | N-5 | 201.4 | No | - | 246.48 | 8.00 | 0.38 | 8.62 | 0.35 | 25.26 | 164.6 | 0.18
2024-03-11 | 2024-12-05 | 0.0 | 0.0 | - | N-4 | 201.43 | No | - | 243.52 | 7.73 | 0.37 | 8.71 | 0.18 | 24.83 | 211.4 | 0.18
2024-03-11 | 2024-12-17 | 0.0 | 0.0 | - | N-3 | 201.44 | No | - | 235.98 | 7.95 | 0.36 | 8.70 | 0.15 | 24.23 | 241.4 | 0.18
| RHMW17 Headspace and Product Gauging | [7 empty] | RHMW17 Parameter Readings
WEEK | DATE | AMBIENT | TOP-OF-CASING HEADSPACE | GROUNDWATER HEADSPACE | TAPE | DTW (Raw) | PRODUCT? | THICKNESS | TDS | pH | Sp. Cond. | D.O. | Turbidity | TEMP | ORP | SAL
|  | (ppmv) | (ppmv) | (ppmv) | (Serial #) | (ft btoc) | (Yes/No) | (ft) | (ppm) |  | (mS/cm) | (mg/L) | (NTU) | (°C) | (Mv) | (psu)
06/12/2023 | 06/15/2023 | 0.0 | 0.0 | - | N-1 | 234.4 | No | - | 286.24 | 7.40 | 0.44 | 2.29 | 0.00 | 24.48 | 46.2 | 0.21
07/03/2023 | 07/07/2023 | 0.0 | 0.0 | - | N-4 | 234.69 | No | - | 264.19 | 7.46 | 0.41 | 2.65 | 0.27 | 24.07 | 65.5 | 0.20
07/31/2023 | 08/04/2023 | 0.0 | 0.0 | - | N-5 | 234.7 | No | - | 257.85 | 7.12 | 0.40 | 3.10 | 0.00 | 24.90 | -6.3 | 0.19
09/04/2023 | 09/08/2023 | 0.0 | 0.0 | - | N-6 | 234.84 | No | - | 261.57 | 7.23 | 0.40 | 3.25 | 0.72 | 25.46 | -26.5 | 0.19
10/02/2023 | 10/04/2023 | 0.0 | 0.0 | - | N-6 | 234.86 | No | - | 245.68 | 7.34 | 0.38 | 3.52 | 0.29 | 25.00 | 245.0 | 0.18
10/23/2023 | 10/25/2023 | 0.0 | 0.1 | - | N-4 | 235.06 | No | - | 250.86 | 7.45 | 0.39 | 3.55 | 2.53 | 23.75 | 219.9 | 0.19
10/30/2023 | 11/02/2023 | 0.0 | 0.0 | - | N-6 | 234.99 | No | - | 249.76 | 7.44 | 0.38 | 3.52 | 1.87 | 24.02 | 258.4 | 0.19
11/06/2023 | 11/08/2023 | 0.0 | 0.0 | - | N-3 | 235.02 | No | - | 240.65 | 7.50 | 0.40 | 3.50 | 0.10 | 23.90 | 232.0 | 0.18
2023-11-13 | 2023-11-15 | 0.0 | 0.0 | - | N-3 | 235.02 | No | - | 248.62 | 7.33 | 0.38 | 3.53 | 0.10 | 24.10 | 271.3 | 0.18
2023-11-20 | 2023-11-22 | 0.0 | 0.0 | - | N-5 | 234.98 | No | - | 241.51 | 7.35 | 0.37 | 3.77 | 0.05 | 24.39 | 262.0 | 0.18
2023-11-27 | 2023-11-28 | 0.0 | 0.0 | - | N-5 | 234.9 | No | - | 244.51 | 7.48 | 0.38 | 3.57 | 0.13 | 23.91 | 263.2 | 0.18
2023-12-04 | 2023-12-06 | 0.0 | 0.3 | - | N-5 | 234.85 | No | - | 244.67 | 7.48 | 0.38 | 3.50 | 0.08 | 23.98 | 198.4 | 0.18
2023-12-11 | 2023-12-12 | 0.0 | 0.0 | - | N-5 | 234.86 | No | - | 251.94 | 7.47 | 0.39 | 3.67 | 0.00 | 23.42 | 230.2 | 0.19
2023-12-18 | 2023-12-19 | 0.0 | 0.8 | - | N-3 | 234.85 | No | - | 240.27 | 7.54 | 0.37 | 3.79 | 0.07 | 23.71 | 252.9 | 0.18
2023-12-25 | 2023-12-27 | 0.0 | 0.0 | - | N-5 | 234.81 | No | - | 256.25 | 7.51 | 0.39 | 3.54 | 0.08 | 23.57 | 220.1 | 0.19
2024-01-01 | 2024-01-03 | 0.0 | 6.7 | - | N-4 | 234.85 | No | - | 260.55 | 7.43 | 0.40 | 3.71 | 0.35 | 24.05 | 265.7 | 0.19
2024-01-08 | 2024-01-09 | 0.0 | 0.0 | - | N-6 | 234.75 | No | - | 247.32 | 7.26 | 0.38 | 3.74 | 0.00 | 24.34 | 267.2 | 0.18
2024-01-15 | 2024-01-16 | 0.0 | 0.0 | - | N-4 | 234.73 | No | - | 206.92 | 7.41 | 0.32 | 3.29 | 0.00 | 24.45 | 238.6 | 0.17
2024-02-05 | 2024-02-09 | 0.0 | 0.0 | - | N-4 | 234.69 | No | - | 235.30 | 7.40 | 0.36 | 4.06 | 0.93 | 23.67 | 243.1 | 0.17
2024-03-18 | 2024-03-18 | 0.0 | 0.0 | - | N-4 | 234.72 | No | - | 256.70 | 7.49 | 0.39 | 4.07 | 0.18 | 23.30 | 220.3 | 0.19
2024-03-18 | 2024-04-10 | 0.0 | 0.0 | - | N-4 | 234.77 | No | - | 230.00 | 7.43 | 0.35 | 4.40 | 0.29 | 24.06 | 260.7 | 0.17
2024-03-18 | 2024-05-13 | 0.0 | 0.0 | 0.0 | N-5 | 234.48 | No | - | 244.10 | 7.49 | 0.38 | 4.06 | 0.38 | 24.19 | 241.7 | 0.18
2024-03-18 | 2024-05-29 | 0.1 | 0.0 | 0.0 | N-3 | 234.3 | No | - | 267.71 | 7.59 | 0.41 | 3.88 | 5.12 | 23.82 | 230.2 | 0.20
2024-03-18 | 2024-06-10 | 0.0 | 0.0 | 0.0 | N-5 | 234.23 | No | - | 245.66 | 6.99 | 0.38 | 3.31 | 0.23 | 25.26 | 260.9 | 0.18
2024-03-18 | 2024-06-24 | 0.0 | 0.0 | 0.0 | N-4 | 234.35 | No | - | 236.85 | 7.58 | 0.36 | 4.22 | 0.83 | 23.88 | 252.7 | 0.18
2024-03-18 | 2024-07-08 | 0.0 | 0.0 | 0.0 | N-5 | 234.25 | No | - | 277.60 | 7.67 | 0.43 | 3.56 | 0.00 | 24.96 | 232.8 | 0.21
2024-03-18 | 2024-07-22 | 0.0 | 0.0 | 0.0 | N-4 | 234.33 | No | - | 243.11 | 7.38 | 0.37 | 4.27 | 0.09 | 24.73 | 165.1 | 0.18
2024-03-18 | 2024-08-12 | 0.0 | 0.0 | 0.0 | N-3 | 234.24 | No | - | 231.37 | 7.55 | 0.36 | 4.33 | 0.10 | 24.73 | 212.2 | 0.17
2024-03-18 | 2024-08-26 | 0.0 | 0.0 | 0.0 | N-4 | 234.3 | No | - | 257.73 | 7.42 | 0.40 | 4.41 | 0.00 | 24.26 | 318.3 | 0.19
2024-03-18 | 2024-09-23 | 0.0 | 0.0 | 0.0 | 252094 | 234.45 | No | - | 266.23 | 7.28 | 0.41 | 1.87 | 3.89 | 24.26 | 267.5 | 0.20
2024-03-18 | 2024-10-14 | 0.0 | 0.0 | 0.0 | N-5 | 234.15 | No | - | 255.98 | 7.46 | 0.39 | 3.45 | 3.62 | 24.24 | 196.3 | 0.19
2024-03-18 | 2024-10-28 | 0.0 | 0.0 | 0.0 | N-4 | 234.18 | No | - | 262.83 | 7.37 | 0.40 | 3.76 | 0.00 | 23.73 | 153.7 | 0.20
2024-03-18 | 2024-11-12 | 0.0 | 0.0 | 0.0 | N-4 | 234.09 | No | - | 263.20 | 7.48 | 0.40 | 3.79 | 0.00 | 23.72 | 135.3 | 0.20
2024-03-18 | 2024-11-22 | 0.0 | 0.0 | 0.0 | N-5 | 234 | No | - | 253.85 | 7.30 | 0.39 | 2.09 | 0.26 | 23.53 | 158.1 | 0.19
2024-03-18 | 2024-12-09 | 0.0 | 0.0 | 0.0 | N-3 | 234.08 | No | - | 243.21 | 7.25 | 0.37 | 4.03 | 0.03 | 23.77 | 153.4 | 0.18
2024-03-18 | 2024-12-20 | 0.0 | 0.0 | 0.0 | N-5 | 234.02 | No | - | 260.68 | 7.36 | 0.40 | 4.06 | 0.07 | 23.98 | 254.2 | 0.19
| RHMW18 Headspace and Product Gauging | [7 empty] | RHMW18 Parameter Readings
WEEK | DATE | AMBIENT | TOP-OF-CASING HEADSPACE | GROUNDWATER HEADSPACE | TAPE | DTW (Raw) | PRODUCT? | THICKNESS | TDS | pH | Sp. Cond. | D.O. | Turbidity | TEMP | ORP | SAL
|  | (ppmv) | (ppmv) | (ppmv) | (Serial #) | (ft btoc) | (Yes/No) | (ft) | (ppm) |  | (mS/cm) | (mg/L) | (NTU) | (°C) | (Mv) | (psu)
2023-12-25 | 2023-12-31 | 0.0 | 0.0 | - | N-6 | 603.83 | No | - | 256.82 | 8.68 | 0.40 | 0.60 | 3.76 | 25.40 | 85.1 | 0.19
2024-01-01 | 2024-01-03 | 0.0 | 0.0 | - | N-6 | 604.69 | No | - | 248.18 | 8.82 | 0.38 | 0.49 | 2.39 | 25.61 | 69.4 | 0.18
2024-01-08 | 2024-01-10 | 0.0 | 0.0 | - | N-6 | 604.67 | No | - | 237.86 | 8.92 | 0.37 | 0.49 | 0.66 | 24.51 | -76.5 | 0.18
2024-01-15 | 2024-01-17 | 0.0 | 0.0 | - | N-6 | 604.64 | No | - | 247.54 | 8.87 | 0.38 | 0.48 | 0.54 | 24.45 | 50.5 | 0.18
2024-02-12 | 2024-02-15 | 0.0 | 0.0 | - | N-6 | 604.54 | No | - | 239.64 | 8.74 | 0.37 | 0.74 | 0.88 | 24.38 | 26.4 | 0.18
2024-03-18 | 2024-03-21 | 0.0 | 0.0 | - | N-6 | 604.6 | No | - | 240.42 | 9.20 | 0.37 | 0.77 | 1.07 | 24.24 | 67.5 | 0.18
2024-03-18 | 2024-04-11 | 0.0 | 0.0 | - | N-6 | 604.67 | No | - | 220.63 | 9.11 | 0.34 | 0.69 | 0.15 | 24.47 | 164.4 | 0.16
2024-03-18 | 2024-05-17 | 0.0 | 0.0 | 0.0 | N-2 | 604.32 | No | - | 214.94 | 9.37 | 0.33 | 1.43 | 0.21 | 24.39 | 135.3 | 0.16
2024-03-18 | 2024-05-30 | 0.0 | 0.0 | 0.0 | N-2 | 604.1 | No | - | 239.71 | 9.28 | 0.37 | 7.34 | 0.00 | 25.39 | 167.2 | 0.18
2024-03-18 | 2024-06-13 | 0.0 | 0.0 | 0.0 | N-7 | 604.25 | No | - | 230.82 | 9.03 | 0.36 | 1.27 | 0.00 | 24.89 | 82.7 | 0.17
2024-03-18 | 2024-06-27 | 0.0 | 0.0 | 0.0 | N-7 | 604.29 | No | - | 221.14 | 9.47 | 0.34 | 1.12 | 0.00 | 24.86 | 96.1 | 0.16
2024-03-18 | 2024-07-11 | 0.0 | 0.0 | 0.0 | N-7 | 604.31 | No | - | 226.99 | 9.35 | 0.35 | 1.40 | 0.00 | 24.69 | 82.1 | 0.17
2024-03-18 | 2024-07-25 | 0.0 | 0.0 | 0.0 | N-7 | 604.34 | No | - | 222.93 | 9.33 | 0.34 | 1.65 | 0.00 | 24.79 | 111.9 | 0.17
2024-03-18 | 2024-08-15 | 0.0 | 0.0 | 0.0 | N-7 | 604.27 | No | - | 231.18 | 9.33 | 0.36 | 1.15 | 0.03 | 25.24 | 89.7 | 0.17
2024-03-18 | 2024-08-29 | 0.0 | 0.0 | 0.0 | N-7 | 604.25 | No | - | 221.96 | 9.40 | 0.34 | 1.85 | 0.12 | 25.09 | 126.5 | 0.16
2024-03-18 | 2024-09-13 | 0.0 | 0.0 | 0.0 | 288404 | 604 | No | - | 241.65 | 9.52 | 0.37 | 1.67 | 0.40 | 25.12 | 128.4 | 0.18
2024-03-18 | 2024-09-25 | 0.0 | 0.0 | 0.0 | N-7 | 604.2 | No | - | 228.61 | 9.33 | 0.35 | 1.08 | 0.07 | 25.35 | 73.9 | 0.17
2024-03-18 | 2024-10-17 | 0.0 | 0.0 | 0.0 | N-7 | 604.25 | No | - | 222.86 | 9.02 | 0.34 | 1.75 | 0.83 | 25.13 | 108.3 | 0.17
2024-03-18 | 2024-10-30 | 0.0 | 0.0 | 0.0 | N-7 | 604.15 | No | - | 243.15 | 9.51 | 0.37 | 1.17 | 0.27 | 24.81 | 48.9 | 0.18
2024-03-18 | 2024-11-14 | 0.0 | 0.0 | 0.0 | N-7 | 604.08 | No | - | 218.62 | 9.61 | 0.34 | 1.25 | 0.00 | 24.18 | -11.8 | 0.16
2024-03-18 | 2024-11-26 | 0.0 | 0.0 | 0.0 | N-7 | 603.97 | No | - | 233.68 | 9.51 | 0.36 | 1.17 | 0.23 | 24.87 | 100.7 | 0.17
2024-03-18 | 2024-12-12 | 0.0 | 0.0 | 0.0 | N-7 | 604.01 | No | - | 275.86 | 9.44 | 0.42 | 1.30 | 0.07 | 24.47 | 30.1 | 0.21
2024-03-18 | 2024-12-26 | 0.0 | 0.0 | 0.0 | N-7 | 603.93 | No | - | 220.13 | 9.44 | 0.34 | 1.87 | 0.41 | 24.66 | 166.9 | 0.16
| RHMW19 Headspace and Product Gauging | [7 empty] | RHMW19 Parameter Readings
WEEK | DATE | AMBIENT | TOP-OF-CASING HEADSPACE | GROUNDWATER HEADSPACE | TAPE | DTW (Raw) | PRODUCT? | THICKNESS | TDS | pH | Sp. Cond. | D.O. | Turbidity | TEMP | ORP | SAL
|  | (ppmv) | (ppmv) | (ppmv) | (Serial #) | (ft btoc) | (Yes/No) | (ft) | (ppm) |  | (mS/cm) | (mg/L) | (NTU) | (°C) | (Mv) | (psu)
06/12/2023 | 06/13/2023 | 0.0 | 0.0 | - | N-6 | 426.5 | No | - | 185.44 | 7.72 | 0.29 | 9.28 | 0.00 | 24.10 | 156.7 | 0.14
07/03/2023 | 07/06/2023 | 0.0 | 0.0 | - | N-6 | 426.9 | No | - | 181.73 | 7.74 | 0.28 | 8.69 | 0.74 | 25.49 | 148.6 | 0.13
07/31/2023 | 08/01/2023 | 0.0 | 0.0 | - | N-5 | 426.96 | No | - | 185.92 | 7.72 | 0.29 | 8.48 | 0.39 | 25.41 | 49.0 | 0.14
09/04/2023 | 09/05/2023 | 0.0 | 0.0 | - | N-5 | 427.09 | No | - | 175.35 | 7.65 | 0.27 | 7.96 | 4.42 | 26.14 | 102.5 | 0.13
10/02/2023 | 10/05/2023 | 0.0 | 0.0 | - | N-6 | 427.19 | No | - | 182.94 | 7.19 | 0.28 | 8.78 | 0.09 | 24.86 | 247.9 | 0.14
10/23/2023 | 10/24/2023 | 0.0 | 0.0 | - | N-6 | 427.26 | No | - | 177.73 | 7.73 | 0.27 | 8.47 | 0.00 | 25.47 | 137.7 | 0.13
10/30/2023 | 10/30/2023 | 0.0 | 0.0 | - | N-4 | 427.27 | No | - | 177.48 | 7.79 | 0.27 | 8.57 | 0.34 | 25.39 | 264.2 | 0.13
11/06/2023 | 11/06/2023 | 0.0 | 0.0 | - | N-6 | 427.29 | No | - | 185.00 | 7.57 | 0.30 | 8.40 | 3.06 | 25.54 | 282.5 | 0.14
2023-11-13 | 2023-11-14 | 0.0 | 0.0 | - | N-6 | 427.3 | No | - | 188.81 | 7.68 | 0.29 | 8.39 | 0.00 | 24.78 | 283.4 | 0.14
2023-11-20 | 2023-11-20 | 0.0 | 0.0 | - | N-3 | 427.24 | No | - | 181.77 | 7.65 | 0.28 | 8.52 | 0.70 | 25.09 | 181.7 | 0.13
2023-11-27 | 2023-11-27 | 0.0 | 0.0 | - | N-5 | 427.2 | No | - | 187.39 | 7.72 | 0.29 | 8.58 | 1.31 | 25.04 | 267.7 | 0.14
2023-12-04 | 2023-12-04 | 0.0 | 0.0 | - | N-4 | 427.21 | No | - | 178.40 | 7.69 | 0.27 | 8.48 | 0.55 | 25.44 | 263.1 | 0.13
2023-12-11 | 2023-12-12 | 0.0 | 0.0 | - | N-4 | 427.15 | No | - | 182.36 | 7.64 | 0.28 | 8.27 | 0.43 | 25.41 | 282.7 | 0.13
2023-12-18 | 2023-12-19 | 0.0 | 0.0 | - | N-6 | 427.14 | No | - | 181.37 | 7.73 | 0.28 | NC | 0.28 | 24.24 | 284.7 | 0.13
2023-12-25 | 2023-12-27 | 0.0 | 0.0 | - | N-4 | 427.06 | No | - | 178.52 | 7.74 | 0.27 | 9.19 | 0.26 | 25.31 | 280.3 | 0.13
2024-01-01 | 2024-01-04 | 0.0 | 0.0 | - | N-4 | 427.03 | No | - | 187.18 | 7.63 | 0.29 | 8.52 | 0.55 | 24.90 | 286.5 | 0.14
2024-01-08 | 2024-01-09 | 0.0 | 0.0 | - | N-4 | 427.02 | No | - | 186.70 | 7.26 | 0.29 | 8.58 | 0.17 | 24.47 | 322.4 | 0.14
2024-01-15 | 2024-01-16 | 0.0 | 0.0 | - | N-5 | 426.91 | No | - | 186.94 | 7.69 | 0.29 | 8.58 | 0.07 | 24.61 | 237.0 | 0.14
2024-02-05 | 2024-02-07 | 0.1 | 0.1 | - | N-4 | 426.97 | No | - | 182.85 | 7.63 | 0.28 | 8.66 | 1.17 | 24.76 | 190.6 | 0.14
2024-03-11 | 2024-03-12 | 0.0 | 0.0 | - | N-6 | 426.93 | No | - | 178.95 | 7.67 | 0.28 | 8.58 | 0.83 | 24.85 | 220.9 | 0.13
2024-03-11 | 2024-04-02 | 0.0 | 0.0 | - | N-6 | 426.99 | No | - | 171.28 | 7.63 | 0.26 | 8.62 | 0.89 | 25.19 | 253.0 | 0.13
2024-03-11 | 2024-05-07 | 0.0 | 0.0 | 0.0 | N-5 | 426.7 | No | - | 176.87 | 7.65 | 0.27 | 8.65 | 0.35 | 24.66 | 216.9 | 0.13
2024-03-11 | 2024-05-21 | 0.0 | 0.0 | 0.0 | N-5 | 426.46 | No | - | 172.57 | 7.60 | 0.27 | 8.62 | 0.00 | 24.85 | 333.2 | 0.13
2024-03-11 | 2024-06-04 | 0.0 | 0.0 | 0.0 | N-3 | 426.41 | No | - | 181.29 | 7.58 | 0.28 | 8.68 | 0.06 | 24.93 | 214.7 | 0.13
2024-03-11 | 2024-06-18 | 0.0 | 0.0 | 0.0 | N-3 | 426.54 | No | - | 190.50 | 7.74 | 0.29 | 8.52 | 0.09 | 24.06 | 222.1 | 0.14
2024-03-11 | 2024-07-02 | 0.0 | 0.0 | 0.0 | N-3 | 426.54 | No | - | 172.50 | 7.74 | 0.27 | 8.70 | 0.01 | 24.60 | 248.4 | 0.13
2024-03-11 | 2024-07-16 | 0.0 | 0.0 | 0.0 | N-4 | 426.68 | No | - | 179.99 | 7.75 | 0.28 | 8.96 | 0.23 | 24.94 | 221.4 | 0.13
2024-03-11 | 2024-08-09 | 0.0 | 0.0 | 0.0 | N-3 | 426.44 | No | - | 194.16 | 7.71 | 0.30 | 8.59 | 0.00 | 24.64 | 283.8 | 0.14
2024-03-11 | 2024-08-23 | 0.0 | 0.0 | 0.0 | N-3 | 426.44 | No | - | 193.66 | 7.76 | 0.30 | 8.51 | 0.00 | 24.72 | 337.3 | 0.14
2024-03-11 | 2024-09-06 | 0.0 | 0.0 | 0.0 | N-5 | 426.36 | No | - | 196.00 | 7.72 | 0.30 | 8.68 | 0.00 | 25.53 | 314.7 | 0.14
2024-03-11 | 2024-10-11 | 0.0 | 0.0 | 0.0 | N-5 | 426.34 | No | - | 193.04 | 7.74 | 0.30 | 8.57 | 2.57 | 25.53 | 282.3 | 0.14
2024-03-11 | 2024-10-25 | 0.0 | 0.0 | 0.0 | N-4 | 426.39 | No | - | 170.23 | 8.25 | 0.26 | 8.66 | 0.23 | 25.50 | 26.2 | 0.13
2024-03-11 | 2024-11-08 | 0.0 | 0.0 | 0.0 | N-3 | 426.24 | No | - | 251.55 | 7.73 | 0.39 | 8.64 | 0.00 | 24.08 | 141.1 | 0.19
2024-03-11 | 2024-11-22 | 0.0 | 0.0 | 0.0 | N-3 | 426.12 | No | - | 183.87 | 7.70 | 0.28 | 8.64 | 0.47 | 24.49 | 157.0 | 0.14
2024-03-11 | 2024-12-06 | 0.0 | 0.0 | 0.0 | N-4 | 426.24 | No | - | 181.58 | 7.63 | 0.28 | 8.71 | 0.18 | 24.24 | 144.1 | 0.13
2024-03-11 | 2024-12-20 | 0.0 | 0.0 | 0.0 | N-3 | 426.12 | No | - | 196.81 | 7.66 | 0.30 | 8.35 | 0.44 | 25.28 | 54.0 | 0.15
| RHMW20 Headspace and Product Gauging | [7 empty] | RHMW20 Parameter Readings
WEEK | DATE | AMBIENT | TOP-OF-CASING HEADSPACE | GROUNDWATER HEADSPACE | TAPE | DTW (Raw) | PRODUCT? | THICKNESS | TDS | pH | Sp. Cond. | D.O. | Turbidity | TEMP | ORP | SAL
|  | (ppmv) | (ppmv) | (ppmv) | (Serial #) | (ft btoc) | (Yes/No) | (ft) | (ppm) |  | (mS/cm) | (mg/L) | (NTU) | (°C) | (Mv) | (psu)
06/12/2023 | 06/14/2023 | 0.0 | 0.0 | - | N-3 | 237.61 | No | - | 1022.20 | 7.47 | 1.57 | 3.91 | 0.37 | 25.53 | 138.8 | 0.80
07/03/2023 | 07/06/2023 | 0.0 | 0.0 | - | N-6 | 237.92 | No | - | 1082.32 | 7.24 | 1.67 | 3.73 | 0.17 | 25.71 | 205.2 | 0.85
07/31/2023 | 08/02/2023 | 0.0 | 0.0 | - | N-4 | 238.19 | No | - | 1152.23 | 7.25 | 1.77 | 3.95 | 10.41 | 28.97 | 95.1 | 0.91
09/04/2023 | 09/06/2023 | 0.0 | 0.0 | - | N-5 | 238.19 | No | - | 1137.23 | 7.25 | 1.75 | 4.53 | 0.13 | 24.59 | 162.6 | 0.90
10/02/2023 | 10/05/2023 | 0.0 | 1.2 | - | N-6 | 238.18 | No | - | 1124.83 | 7.09 | 1.73 | 4.95 | 0.00 | 25.32 | 238.8 | 0.89
10/23/2023 | 10/23/2023 | 0.0 | 0.0 | - | N-3 | 238.24 | No | - | 1176.44 | 7.22 | 1.81 | 5.21 | 0.07 | 25.14 | 114.0 | 0.93
10/30/2023 | 11/02/2023 | 0.0 | 0.2 | - | N-6 | 238.31 | No | - | 1184.39 | 7.21 | 1.82 | 5.26 | 0.76 | 25.03 | 274.1 | 0.94
11/06/2023 | 11/09/2023 | 0.0 | 0.0 | - | N-6 | 238.36 | No | - | 1152.62 | 7.23 | 1.80 | 5.40 | 0.18 | 24.63 | 242.6 | 0.91
2023-11-13 | 2023-11-14 | 0.0 | 0.0 | - | N-4 | 238.45 | No | - | 1201.23 | 7.20 | 1.85 | 5.28 | 0.08 | 24.20 | 110.8 | 0.95
2023-11-20 | 2023-11-21 | 0.1 | 0.1 | - | N-5 | 238.35 | No | - | 1120.25 | 7.22 | 1.72 | 5.64 | 0.30 | 24.28 | 262.1 | 0.88
2023-11-27 | 2023-11-29 | 0.0 | 0.0 | - | N-5 | 238.26 | No | - | 1120.08 | 7.25 | 1.72 | 5.42 | 0.00 | 23.85 | 244.9 | 0.88
2023-12-04 | 2023-12-07 | 0.0 | 0.0 | - | N-4 | 238.22 | No | - | 1193.57 | 7.22 | 1.84 | 5.08 | 0.11 | 24.80 | 250.1 | 0.94
2023-12-11 | 2023-12-13 | 0.0 | 0.0 | - | N-3 | 238.24 | No | - | 1144.19 | 7.22 | 1.76 | 5.29 | 0.00 | 24.26 | 249.2 | 0.90
2023-12-18 | 2023-12-20 | 0.0 | 0.0 | - | N-4 | 238.24 | No | - | 1150.96 | 7.22 | 1.77 | 5.36 | 0.11 | 23.42 | 261.9 | 0.91
2023-12-25 | 2023-12-28 | 0.0 | 0.0 | - | N-3 | 238.16 | No | - | 1193.73 | 7.23 | 1.84 | 5.33 | 0.32 | 23.68 | 263.6 | 0.94
2024-01-01 | 2024-01-03 | 0.0 | 0.0 | - | N-3 | 238.12 | No | - | 1192.03 | 7.24 | 1.83 | 5.42 | 0.00 | 24.10 | 254.3 | 0.94
2024-01-08 | 2024-01-10 | 0.0 | 0.0 | - | N-4 | 238.15 | No | - | 1194.14 | 7.21 | 1.84 | 5.12 | 0.17 | 23.61 | 229.3 | 0.94
2024-01-15 | 2024-01-17 | 0.0 | 0.0 | - | N-5 | 238.07 | No | - | 1159.87 | 7.20 | 1.78 | 5.46 | 1.62 | 23.71 | 263.3 | 0.92
2024-02-05 | 2024-02-09 | 0.0 | 0.0 | - | N-4 | 238.02 | No | - | 1165.74 | 7.15 | 1.79 | 5.77 | 0.75 | 23.45 | 234.3 | 0.92
2024-03-18 | 2024-03-22 | 0.0 | 0.0 | - | N-4 | 238.15 | No | - | 1221.86 | 7.13 | 1.88 | 5.95 | 0.83 | 24.26 | 247.0 | 0.97
2024-03-18 | 2024-04-12 | 0.0 | 0.0 | - | N-4 | 238.1 | No | - | 1236.66 | 7.11 | 1.90 | 5.96 | 0.00 | 24.35 | 127.8 | 0.98
2024-03-18 | 2024-05-16 | 0.0 | 0.0 | 0.0 | N-3 | 237.73 | No | - | 1129.34 | 7.14 | 1.74 | 6.10 | 0.01 | 23.81 | 306.5 | 0.89
2024-03-18 | 2024-05-31 | 0.0 | 0.0 | 0.0 | N-3 | 237.64 | No | - | 1175.10 | 7.08 | 1.81 | 6.07 | 0.12 | 24.25 | 269.8 | 0.93
2024-03-18 | 2024-06-14 | 0.0 | 0.0 | 0.0 | N-4 | 237.66 | No | - | 1232.41 | 7.11 | 1.90 | 6.16 | 0.00 | 24.66 | 281.2 | 0.98
2024-03-18 | 2024-06-26 | 0.0 | 0.0 | 0.0 | N-3 | 237.63 | No | - | 1278.03 | 7.11 | 1.97 | 6.13 | 0.24 | 25.18 | 303.2 | 1.01
2024-03-18 | 2024-07-09 | 0.0 | 0.0 | 0.0 | N-3 | 237.6 | No | - | 1268.98 | 6.94 | 1.95 | 6.68 | 0.64 | 25.30 | 233.6 | 1.01
2024-03-18 | 2024-07-23 | 0.0 | 0.0 | 0.0 | N-5 | 237.58 | No | - | 1234.00 | 7.12 | 1.90 | 6.43 | 0.00 | 25.31 | 250.4 | 0.98
2024-03-18 | 2024-08-13 | 0.0 | 0.0 | 0.0 | N-4 | 237.7 | No | - | 1170.62 | 7.12 | 1.80 | 6.46 | 0.00 | 24.68 | 229.6 | 0.92
2024-03-18 | 2024-08-28 | 0.0 | 0.0 | 0.0 | N-5 | 237.61 | No | - | 1237.68 | 7.12 | 1.90 | 6.45 | 0.97 | 24.93 | 312.3 | 0.98
2024-03-18 | 2024-09-24 | 0.0 | 0.0 | 0.0 | N-5 | 237.53 | No | - | 1245.10 | 7.03 | 1.92 | 6.35 | 0.00 | 24.65 | 306.7 | 0.99
2024-03-18 | 2024-10-16 | 0.0 | 0.0 | 0.0 | N-5 | 237.43 | No | - | 1185.36 | 7.05 | 1.82 | 6.68 | 0.21 | 24.71 | 278.4 | 0.94
2024-03-18 | 2024-10-31 | 0.0 | 0.0 | 0.0 | N-3 | 237.44 | No | - | 1249.20 | 7.00 | 1.92 | 6.48 | 0.00 | 24.40 | 120.6 | 0.99
2024-03-18 | 2024-11-13 | 0.0 | 0.0 | 0.0 | N-5 | 237.4 | No | - | 1240.87 | 7.03 | 1.91 | 6.66 | 0.00 | 23.82 | 121.1 | 0.98
2024-03-18 | 2024-11-26 | 0.0 | 0.0 | 0.0 | N-4 | 237.35 | No | - | 1263.67 | 7.11 | 1.94 | 6.38 | 0.32 | 24.45 | 208.5 | 1.00
2024-03-18 | 2024-12-11 | 0.0 | 0.0 | 0.0 | N-3 | 237.33 | No | - | 1243.57 | 7.09 | 1.91 | 6.55 | 0.19 | 24.22 | 284.5 | 0.98
2024-03-18 | 2024-12-27 | 0.0 | 0.0 | 0.0 | N-3 | 237.31 | No | - | 1220.02 | 7.04 | 1.88 | 6.67 | 0.55 | 24.16 | 206.6 | 0.97
| RHMW21 Headspace and Product Gauging | [7 empty] | RHMW21 Parameter Readings
WEEK | DATE | AMBIENT | TOP-OF-CASING HEADSPACE | GROUNDWATER HEADSPACE | TAPE | DTW (Raw) | PRODUCT? | THICKNESS | TDS | pH | Sp. Cond. | D.O. | Turbidity | TEMP | ORP | SAL
|  | (ppmv) | (ppmv) | (ppmv) | (Serial #) | (ft btoc) | (Yes/No) | (ft) | (ppm) |  | (mS/cm) | (mg/L) | (NTU) | (°C) | (Mv) | (psu)
06/12/2023 | 2024-07-22 | 0.0 | 0.0 | 0.0 | N-3 | 115.34 | No | - | 256.48 | 10.51 | 0.39 | 0.29 | 0.00 | 25.89 | -52.1 | 0.19
06/12/2023 | 2024-08-05 | 0.0 | 0.0 | 0.0 | N-3 | 113.68 | No | - | 225.15 | 10.36 | 0.35 | 0.46 | 0.11 | 25.02 | -32.9 | 0.17
06/12/2023 | 2024-08-22 | 0.0 | 0.0 | 0.0 | N-5 | 113.73 | No | - | 208.10 | 10.09 | 0.32 | 0.29 | 0.02 | 24.77 | -18.9 | 0.15
06/12/2023 | 2024-09-04 | 0.0 | 0.1 | 0.0 | N-5 | 113.6 | No | - | 223.26 | 10.12 | 0.34 | 0.44 | 0.22 | 24.65 | -57.4 | 0.17
06/12/2023 | 2024-09-16 | 0.0 | 0.5 | 0.0 | 252094 | 113.5 | No | - | 200.71 | 9.99 | 0.31 | 0.37 | 0.32 | 24.94 | 20.1 | 0.15
06/12/2023 | 2024-10-07 | 0.0 | 0.0 | 0.0 | N-4 | 113.61 | No | - | 229.96 | 9.97 | 0.35 | 0.38 | 2.73 | 24.57 | 93.2 | 0.17
06/12/2023 | 2024-10-21 | 0.0 | 0.2 | 0.0 | N-3 | 113.47 | No | - | 203.56 | 9.96 | 0.31 | 0.31 | 0.86 | 24.69 | -68.8 | 0.15
06/12/2023 | 2024-11-04 | 0.0 | 0.2 | 0.0 | N-1 | 113.41 | No | - | 202.56 | 10.17 | 0.31 | 0.43 | 0.88 | 24.44 | -281.3 | 0.15
06/12/2023 | 2024-11-18 | 0.0 | 0.0 | 0.0 | N-5 | 113.37 | No | - | 233.65 | 9.84 | 0.36 | 0.29 | 0.19 | 24.40 | -233.4 | 0.17
06/12/2023 | 2024-12-02 | 0.0 | 0.0 | 0.0 | N-3 | 113.45 | No | - | 192.88 | 9.76 | 0.30 | 0.36 | 0.72 | 24.31 | -219.0 | 0.14
06/12/2023 | 2024-12-16 | 0.0 | 0.0 | 0.0 | N-3 | 113.45 | No | - | 199.35 | 9.66 | 0.31 | 0.38 | 0.47 | 24.44 | -280.4 | 0.15
| RHMW2254-01 Headspace and Product Gauging | [7 empty] | RHMW2254-01 Parameter Readings
WEEK | DATE | AMBIENT | TOP-OF-CASING HEADSPACE | GROUNDWATER HEADSPACE | TAPE | DTW (Raw) | PRODUCT? | THICKNESS | TDS | pH | Sp. Cond. | D.O. | Turbidity | TEMP | ORP | SAL
|  | (ppmv) | (ppmv) | (ppmv) | (Serial #) | (ft btoc) | (Yes/No) | (ft) | (ppm) |  | (mS/cm) | (mg/L) | (NTU) | (°C) | (Mv) | (psu)
06/05/2023 | 06/08/2023 | 0.0 | 0.0 | - | N-4 | 88.39 | No | - | 361.41 | 7.60 | 0.56 | 8.91 | 0.09 | 22.23 | 175.8 | 0.27
07/03/2023 | 07/03/2023 | 0.0 | 0.0 | - | N-4 | 88.66 | No | - | 360.16 | 7.66 | 0.55 | 8.65 | 0.00 | 22.26 | 278.6 | 0.27
07/31/2023 | 08/02/2023 | 0.0 | 0.0 | - | N-6 | 88.66 | No | - | 366.47 | 7.57 | 0.56 | 8.76 | 0.03 | 22.42 | 103.9 | 0.28
09/04/2023 | 09/06/2023 | 0.1 | 0.0 | - | N-4 | 88.72 | No | - | 393.05 | 7.32 | 0.60 | 8.67 | 0.00 | 22.26 | 147.0 | 0.30
10/02/2023 | 10/05/2023 | 0.0 | 0.0 | - | N-4 | 88.13 | No | - | 389.40 | 7.21 | 0.60 | 8.66 | 0.00 | 21.99 | 287.2 | 0.29
10/16/2023 | 10/17/2023 | 0.0 | 0.0 | - | N-4 | 88.83 | No | - | 381.48 | 7.43 | 0.59 | 8.49 | 0.00 | 22.14 | 230.0 | 0.29
10/23/2023 | 10/24/2023 | 0.0 | 0.0 | - | N-4 | 88.84 | No | - | 378.77 | 7.62 | 0.58 | 8.68 | 0.21 | 22.04 | 245.6 | 0.29
10/30/2023 | 10/31/2023 | 0.0 | 0.0 | - | N-3 | 88.77 | No | - | 386.82 | 7.59 | 0.60 | 8.43 | 0.08 | 22.15 | 278.8 | 0.29
11/06/2023 | 11/07/2023 | 0.0 | 0.0 | - | N-4 | 89.01 | No | - | 377.63 | 7.63 | 0.60 | 8.40 | 0.00 | 22.25 | 282.6 | 0.28
2023-11-13 | 2023-11-14 | 0.0 | 0.0 | - | N-3 | 88.82 | No | - | 379.45 | 7.60 | 0.58 | 8.68 | 0.00 | 22.38 | 268.4 | 0.29
2023-11-20 | 2023-11-21 | 0.1 | 0.1 | - | N-5 | 88.9 | No | - | 381.48 | 7.58 | 0.59 | 9.09 | 0.22 | 21.84 | 278.6 | 0.29
2023-11-27 | 2023-11-28 | 0.0 | 0.0 | - | N-5 | 88.75 | No | - | 374.41 | 7.62 | 0.58 | 8.91 | 0.13 | 22.10 | 297.1 | 0.28
2023-12-04 | 2023-12-05 | 0.0 | 0.0 | - | N-5 | 88.68 | No | - | 380.87 | 7.56 | 0.59 | 8.63 | 0.00 | 22.35 | 286.3 | 0.29
2023-12-11 | 2023-12-12 | 0.0 | 0.0 | - | N-6 | 88.85 | No | - | 376.00 | 7.59 | 0.58 | 8.72 | 0.02 | 22.15 | 241.7 | 0.28
2023-12-18 | 2023-12-19 | 0.0 | 0.0 | - | N-4 | 88.73 | No | - | 372.18 | 7.65 | 0.57 | 8.69 | 0.07 | 21.92 | 232.9 | 0.28
2023-12-25 | 2023-12-26 | 0.0 | 0.0 | - | N-4 | 88.69 | No | - | 365.98 | 7.53 | 0.56 | 8.68 | 0.00 | 21.97 | 185.8 | 0.28
2024-01-01 | 2024-01-02 | 0.0 | 0.0 | - | N-5 | 88.61 | No | - | 384.59 | 7.53 | 0.59 | 8.69 | 0.37 | 22.18 | 300.0 | 0.29
2024-01-08 | 2024-01-09 | 0.0 | 0.0 | - | N-5 | 88.54 | No | - | 385.96 | 7.55 | 0.59 | 8.64 | 0.00 | 22.23 | 296.7 | 0.29
2024-01-15 | 2024-01-16 | 0.0 | 0.0 | - | N-4 | 88.57 | No | - | 315.54 | 7.57 | 0.49 | 8.67 | 0.00 | 21.95 | 255.4 | 0.26
2024-02-12 | 2024-02-13 | 0.0 | 0.0 | - | N-4 | 88.47 | No | - | 380.47 | 7.58 | 0.59 | 8.55 | 0.59 | 21.91 | 258.9 | 0.29
2024-03-11 | 2024-03-15 | 0.0 | 0.0 | - | N-4 | 88.58 | No | - | 379.02 | 7.51 | 0.58 | 8.60 | 0.31 | 21.80 | 282.4 | 0.29
2024-03-11 | 2024-04-02 | 0.2 | 0.2 | - | N-5 | 88.78 | No | - | 387.49 | 7.50 | 0.60 | 8.20 | 0.09 | 22.17 | 212.6 | 0.29
2024-03-11 | 2024-05-07 | 0.0 | 0.0 | 0.0 | N-4 | 88.55 | No | - | 392.28 | 7.62 | 0.60 | 8.49 | 0.00 | 22.04 | 273.7 | 0.30
2024-03-11 | 2024-05-24 | 0.0 | 0.0 | 0.0 | N-5 | 88.22 | No | - | 351.08 | 7.75 | 0.54 | 8.68 | 0.09 | 22.06 | 373.2 | 0.26
2024-03-11 | 2024-06-04 | 0.0 | 0.0 | 0.0 | N-5 | 87.94 | No | - | 359.80 | 7.61 | 0.55 | 8.18 | 0.00 | 22.31 | 275.3 | 0.27
2024-03-11 | 2024-06-19 | 0.0 | 0.0 | 0.0 | N-3 | 88.23 | No | - | 335.78 | 7.24 | 0.52 | 8.68 | 0.42 | 22.36 | 301.3 | 0.25
2024-03-11 | 2024-07-02 | 0.0 | 0.0 | 0.0 | N-5 | 88.25 | No | - | 351.64 | 7.42 | 0.54 | 8.57 | 0.00 | 22.29 | 298.3 | 0.26
2024-03-11 | 2024-07-16 | 0.0 | 0.0 | 0.0 | N-3 | 88.25 | No | - | 363.95 | 7.59 | 0.56 | 8.70 | 0.00 | 22.38 | 215.9 | 0.27
2024-03-11 | 2024-08-06 | 0.0 | 0.0 | 0.0 | N-5 | 88.23 | No | - | 335.63 | 7.51 | 0.52 | 8.62 | 0.00 | 22.32 | 211.2 | 0.25
2024-03-11 | 2024-08-20 | 0.0 | 0.0 | 0.0 | N-5 | 88.24 | No | - | 317.59 | 7.85 | 0.49 | 8.68 | 0.00 | 22.35 | 232.2 | 0.24
2024-03-11 | 2024-09-04 | 0.0 | 0.0 | 0.0 | N-5 | 88.05 | No | - | 340.32 | 7.55 | 0.52 | 8.58 | 0.04 | 22.53 | 210.2 | 0.26
2024-03-11 | 2024-09-17 | 0.0 | 0.0 | 0.0 | 252094 | 88.08 | No | - | 335.58 | 7.50 | 0.52 | 9.31 | 0.00 | 22.55 | 266.7 | 0.25
2024-03-11 | 2024-10-08 | 0.0 | 0.0 | 0.0 | N-4 | 88.08 | No | - | 360.31 | 7.43 | 0.55 | 9.14 | 0.00 | 22.33 | 277.3 | 0.27
2024-03-11 | 2024-10-22 | 0.0 | 0.0 | 0.0 | N-4 | 87.55 | No | - | 358.58 | 7.55 | 0.55 | 7.68 | 0.00 | 22.69 | 186.6 | 0.27
2024-03-11 | 2024-11-05 | 0.0 | 0.0 | 0.0 | N-3 | 87.96 | No | - | 323.65 | 7.92 | 0.50 | 8.62 | 0.00 | 22.23 | 69.3 | 0.24
2024-03-11 | 2024-11-19 | 0.0 | 0.0 | 0.0 | N-3 | 87.84 | No | - | 315.56 | 7.57 | 0.49 | 8.65 | 0.00 | 22.17 | 196.3 | 0.24
2024-03-11 | 2024-12-06 | 0.0 | 0.0 | 0.0 | N-3 | 87.77 | No | - | 297.27 | 7.58 | 0.46 | 8.58 | 0.13 | 22.18 | 219.4 | 0.22
2024-03-11 | 2024-12-26 | 0.0 | 0.0 | 0.0 | N-5 | 87.08 | No | - | 325.89 | 7.48 | 0.50 | 8.71 | 0.00 | 22.12 | 206.4 | 0.24
| RHP01 Headspace and Product Gauging | [7 empty] | RHP01 Parameter Readings
WEEK | DATE | AMBIENT | TOP-OF-CASING HEADSPACE | GROUNDWATER HEADSPACE | TAPE | DTW (Raw) | PRODUCT? | THICKNESS | TDS | pH | Sp. Cond. | D.O. | Turbidity | TEMP | ORP | SAL
|  | (ppmv) | (ppmv) | (ppmv) | (Serial #) | (ft btoc) | (Yes/No) | (ft) | (ppm) |  | (mS/cm) | (mg/L) | (NTU) | (°C) | (Mv) | (psu)
06/12/2023 | 06/16/2023 | 0.0 | 0.0 | - | N-1 | 138.55 | No | - | 439.50 | 6.91 | 0.68 | 6.86 | 0.00 | 24.78 | 101.5 | 0.33
07/03/2023 | 07/06/2023 | 0.0 | 0.0 | - | N-3 | 139.56 | No | - | 426.86 | 6.89 | 0.66 | 7.43 | 0.09 | 24.72 | 186.2 | 0.32
07/31/2023 | 08/02/2023 | 0.0 | 0.0 | - | N-5 | 139.59 | No | - | 422.90 | 6.75 | 0.65 | 6.70 | 0.13 | 27.57 | 164.6 | 0.32
09/04/2023 | 09/06/2023 | 0.0 | 0.0 | - | N-6 | 139.66 | No | - | 409.47 | 6.70 | 0.63 | 7.07 | 0.13 | 25.43 | 111.2 | 0.31
10/02/2023 | 10/04/2023 | 0.0 | 0.0 | - | N-5 | 139.66 | No | - | 448.74 | 6.84 | 0.69 | 6.54 | 10.74 | 24.76 | 247.4 | 0.34
10/23/2023 | 10/25/2023 | 0.0 | 0.0 | - | N-6 | 139.81 | No | - | 417.67 | 6.89 | 0.64 | 6.70 | 0.00 | 25.04 | 154.2 | 0.32
10/30/2023 | 11/01/2023 | 0.0 | 0.0 | - | N-3 | 139.74 | No | - | 427.69 | 6.99 | 0.66 | 6.80 | 0.28 | 24.57 | 296.3 | 0.32
11/06/2023 | 11/06/2023 | 0.0 | 0.0 | - | N-4 | 139.83 | No | - | 413.38 | 6.98 | 0.60 | 6.80 | 0.29 | 25.44 | 254.3 | 0.31
2023-11-13 | 2023-11-13 | 0.0 | 0.0 | - | N-3 | 139.81 | No | - | 413.28 | 6.98 | 0.64 | 6.70 | 0.00 | 24.56 | 231.8 | 0.31
2023-11-20 | 2023-11-20 | 0.0 | 0.0 | - | N-4 | 139.83 | No | - | 412.58 | 7.05 | 0.63 | 6.72 | 0.25 | 24.54 | 289.5 | 0.31
2023-11-27 | 2023-11-29 | 0.0 | 0.0 | - | N-4 | 139.75 | No | - | 411.21 | 6.95 | 0.63 | 6.54 | 0.00 | 24.23 | 303.0 | 0.31
2023-12-04 | 2023-12-04 | 0.0 | 0.0 | - | N-6 | 139.63 | No | - | 411.25 | 6.70 | 0.63 | 6.54 | 0.36 | 24.62 | 246.0 | 0.31
2023-12-11 | 2023-12-11 | 0.0 | 0.0 | - | N-4 | 139.68 | No | - | 409.75 | 6.88 | 0.63 | 6.67 | 0.63 | 24.70 | 273.7 | 0.31
2023-12-18 | 2023-12-18 | 0.0 | 0.0 | - | N-3 | 139.68 | No | - | 420.01 | 7.01 | 0.65 | 6.68 | 0.08 | 23.91 | 205.5 | 0.32
2023-12-25 | 2023-12-26 | 0.0 | 0.0 | - | N-3 | 139.57 | No | - | 411.30 | 6.95 | 0.63 | 6.81 | 0.51 | 24.40 | 272.8 | 0.31
2024-01-01 | 2024-01-02 | 0.0 | 2.5 | - | N-3 | 139.6 | No | - | 419.50 | 6.95 | 0.65 | 6.93 | 0.14 | 24.11 | 274.9 | 0.32
2024-01-08 | 2024-01-08 | 0.0 | 0.0 | - | N-4 | 139.58 | No | - | 423.66 | 6.90 | 0.65 | 6.78 | 0.00 | 24.17 | 329.3 | 0.32
2024-01-15 | 2024-01-15 | 0.0 | 0.0 | - | N-4 | 139.53 | No | - | 419.16 | 6.89 | 0.64 | 6.64 | 0.21 | 23.67 | 249.1 | 0.32
2024-02-05 | 2024-02-08 | 0.0 | 0.0 | - | N-5 | 139.44 | No | - | 426.78 | 6.65 | 0.66 | 6.84 | 0.87 | 23.97 | 189.0 | 0.32
2024-03-11 | 2024-03-11 | 0.0 | 0.0 | - | N-5 | 139.49 | No | - | 445.62 | 6.90 | 0.69 | 6.81 | 0.12 | 24.57 | 180.0 | 0.34
2024-03-11 | 2024-04-01 | 0.0 | 0.1 | - | N-5 | 139.54 | No | - | 431.99 | 6.92 | 0.66 | 6.78 | 0.06 | 23.95 | 278.8 | 0.33
2024-03-11 | 2024-05-06 | 0.0 | 0.0 | 0.0 | N-6 | 139.29 | No | - | 434.82 | 6.98 | 0.67 | 6.86 | 0.01 | 24.92 | 297.0 | 0.33
2024-03-11 | 2024-05-20 | 0.0 | 0.0 | 0.0 | N-5 | 138.46 | No | - | 433.11 | 6.86 | 0.67 | 6.92 | 0.22 | 24.29 | 336.6 | 0.33
2024-03-11 | 2024-06-06 | 0.0 | 0.0 | 0.0 | N-4 | 139.2 | No | - | 426.32 | 6.84 | 0.66 | 6.94 | 0.09 | 24.91 | 243.3 | 0.32
2024-03-11 | 2024-06-20 | 0.0 | 0.0 | 0.0 | N-3 | 139.22 | No | - | 411.18 | 6.90 | 0.63 | 7.04 | 0.49 | 24.54 | 303.0 | 0.31
2024-03-11 | 2024-07-01 | 0.0 | 0.0 | 0.0 | N-5 | 139.03 | No | - | 443.04 | 6.91 | 0.68 | 6.98 | 0.00 | 25.67 | 313.1 | 0.34
2024-03-11 | 2024-07-18 | 0.0 | 0.0 | 0.0 | N-3 | 138.48 | No | - | 461.06 | 6.92 | 0.71 | 6.98 | 0.00 | 25.23 | 270.2 | 0.35
2024-03-11 | 2024-08-08 | 0.0 | 0.0 | 0.0 | N-3 | 138.47 | No | - | 447.30 | 6.90 | 0.69 | 7.25 | 0.00 | 25.17 | 316.7 | 0.34
2024-03-11 | 2024-08-20 | 0.0 | 0.0 | 0.0 | N-3 | 139.18 | No | - | 447.77 | 6.88 | 0.69 | 6.93 | 0.00 | 24.98 | 342.5 | 0.34
2024-03-11 | 2024-09-05 | 0.0 | 0.0 | 0.0 | N-5 | 139.03 | No | - | 448.92 | 6.91 | 0.69 | 6.98 | 0.00 | 24.61 | 295.8 | 0.34
2024-03-11 | 2024-09-19 | 0.0 | 0.0 | 0.0 | 252094 | 138.31 | No | - | 427.66 | 6.96 | 0.66 | 6.71 | 0.51 | 25.84 | 294.8 | 0.32
2024-03-11 | 2024-10-03 | 0.0 | 0.0 | 0.0 | N-4 | 138.33 | No | - | 449.68 | 6.95 | 0.69 | 6.85 | 0.08 | 25.05 | 261.9 | 0.34
2024-03-11 | 2024-10-24 | 0.0 | 0.0 | 0.0 | N-7 | 138.35 | No | - | 435.40 | 6.90 | 0.67 | 6.41 | 0.33 | 25.33 | 148.0 | 0.33
2024-03-11 | 2024-11-07 | 0.0 | 0.0 | 0.0 | N-5 | 138.24 | No | - | 490.07 | 6.87 | 0.75 | 6.10 | 0.07 | 24.50 | 162.1 | 0.37
2024-03-11 | 2024-11-21 | 0.0 | 0.0 | 0.0 | N-5 | 138.18 | No | - | 421.72 | 7.00 | 0.65 | 5.94 | 0.43 | 24.41 | 198.6 | 0.32
2024-03-11 | 2024-12-05 | 0.0 | 0.0 | 0.0 | N-3 | 138.18 | No | - | 410.29 | 6.89 | 0.63 | 6.56 | 0.17 | 24.39 | 224.7 | 0.31
2024-03-11 | 2024-12-19 | 0.0 | 0.0 | 0.0 | N-5 | 138.24 | No | - | 431.63 | 6.86 | 0.66 | 6.60 | 0.28 | 24.11 | 253.7 | 0.33
| RHP02 Headspace and Product Gauging | [7 empty] | RHP02 Parameter Readings
WEEK | DATE | AMBIENT | TOP-OF-CASING HEADSPACE | GROUNDWATER HEADSPACE | TAPE | DTW (Raw) | PRODUCT? | THICKNESS | TDS | pH | Sp. Cond. | D.O. | Turbidity | TEMP | ORP | SAL
|  | (ppmv) | (ppmv) | (ppmv) | (Serial #) | (ft btoc) | (Yes/No) | (ft) | (ppm) |  | (mS/cm) | (mg/L) | (NTU) | (°C) | (Mv) | (psu)
06/12/2023 | 06/16/2023 | 0.0 | 0.0 | - | N-1 | 122.05 | No | - | 493.32 | 6.84 | 0.76 | 7.70 | 0.19 | 25.96 | 107.5 | 0.37
07/03/2023 | 07/06/2023 | 0.0 | 0.0 | - | N-3 | 122.41 | No | - | 478.01 | 6.78 | 0.74 | 7.55 | 0.00 | 25.65 | 185.5 | 0.36
07/31/2023 | 08/02/2023 | 0.0 | 0.0 | - | N-6 | 122.5 | No | - | 461.62 | 6.82 | 0.71 | 7.59 | 0.33 | 25.36 | 148.2 | 0.35
09/04/2023 | 09/06/2023 | 0.0 | 0.0 | - | N-6 | 122.65 | No | - | 461.08 | 6.85 | 0.71 | 7.79 | 0.09 | 25.88 | 131.6 | 0.35
10/02/2023 | 10/06/2023 | 0.0 | 0.9 | - | N-6 | 122.66 | No | - | 472.51 | 7.20 | 0.73 | 0.84 | 1.29 | 25.83 | 212.7 | 0.36
10/23/2023 | 10/25/2023 | 0.0 | 0.0 | - | N-6 | 122.8 | No | - | 477.81 | 6.66 | 0.74 | 7.42 | 0.00 | 25.30 | 205.7 | 0.36
10/30/2023 | 11/01/2023 | 0.0 | 0.0 | - | N-3 | 122.7 | No | - | 484.64 | 6.79 | 0.75 | 7.71 | 0.41 | 25.46 | 321.2 | 0.37
11/06/2023 | 11/08/2023 | 0.0 | 0.0 | - | N-5 | 122.73 | No | - | 473.87 | 6.92 | 0.70 | 7.70 | 0.30 | 24.76 | 255.1 | 0.36
2023-11-13 | 2023-11-14 | 0.0 | 0.0 | - | N-4 | 122.78 | No | - | 479.28 | 6.94 | 0.74 | 7.71 | 0.00 | 24.61 | 204.2 | 0.36
2023-11-20 | 2023-11-22 | 0.0 | 0.0 | - | N-5 | 122.78 | No | - | 464.96 | 6.84 | 0.72 | 7.69 | 0.00 | 24.58 | 298.6 | 0.35
2023-11-27 | 2023-11-27 | 0.0 | 0.0 | - | N-3 | 122.73 | No | - | 461.50 | 6.91 | 0.71 | 8.11 | 0.06 | 24.41 | 273.8 | 0.35
2023-12-04 | 2023-12-06 | 0.0 | 0.0 | - | N-3 | 122.58 | No | - | 473.51 | 6.93 | 0.73 | 7.69 | 0.42 | 24.59 | 271.1 | 0.36
2023-12-11 | 2023-12-11 | 0.0 | 0.0 | - | N-3 | 122.56 | No | - | 456.99 | 6.97 | 0.70 | 8.08 | 0.00 | 24.44 | 274.7 | 0.35
2023-12-18 | 2023-12-18 | 0.0 | 0.0 | - | N-3 | 122.57 | No | - | 470.04 | 7.00 | 0.72 | 7.68 | 0.11 | 24.04 | 268.5 | 0.36
2023-12-25 | 2023-12-26 | 0.0 | 0.0 | - | N-3 | 122.46 | No | - | 460.21 | 6.99 | 0.71 | 7.81 | 0.15 | 24.10 | 261.7 | 0.35
2024-01-01 | 2024-01-02 | 0.0 | 0.0 | - | N-3 | 122.49 | No | - | 469.90 | 6.91 | 0.72 | 7.82 | 0.09 | 24.48 | 284.6 | 0.36
2024-01-08 | 2024-01-08 | 0.0 | 0.0 | - | N-6 | 122.37 | No | - | 474.07 | 6.93 | 0.73 | 7.70 | 0.00 | 24.32 | 312.5 | 0.36
2024-01-15 | 2024-01-15 | 0.0 | 0.0 | - | N-4 | 122.37 | No | - | 469.46 | 6.86 | 0.72 | 7.95 | 0.09 | 24.04 | 267.8 | 0.36
2024-02-05 | 2024-02-08 | 0.0 | 0.1 | - | N-4 | 122.33 | No | - | 448.40 | 6.91 | 0.69 | 7.75 | 0.35 | 24.10 | 230.7 | 0.34
2024-03-11 | 2024-03-14 | 0.0 | 0.0 | - | N-5 | 122.3 | No | - | 454.18 | 6.92 | 0.70 | 7.76 | 0.00 | 24.51 | 299.1 | 0.34
2024-03-11 | 2024-04-04 | 0.0 | 0.0 | - | N-6 | 122.41 | No | - | 489.70 | 6.86 | 0.75 | 7.75 | 0.00 | 24.66 | 302.0 | 0.37
2024-03-11 | 2024-05-09 | 0.0 | 0.0 | 0.0 | N-5 | 121.73 | No | - | 489.97 | 6.92 | 0.75 | 7.71 | 0.30 | 24.52 | 315.3 | 0.37
2024-03-11 | 2024-05-23 | 0.0 | 0.0 | 0.0 | N-3 | 121.6 | No | - | 460.21 | 6.84 | 0.71 | 7.67 | 0.48 | 26.31 | 248.2 | 0.35
2024-03-11 | 2024-06-06 | 0.1 | 0.1 | 0.0 | N-5 | 121.53 | No | - | 491.82 | 6.78 | 0.76 | 7.68 | 0.78 | 26.68 | 324.5 | 0.37
2024-03-11 | 2024-06-20 | 0.0 | 0.0 | 0.0 | N-4 | 121.64 | No | - | 457.91 | 7.17 | 0.70 | 7.69 | 0.18 | 25.60 | 294.4 | 0.35
2024-03-11 | 2024-07-02 | 0.0 | 0.0 | 0.0 | N-4 | 122 | No | - | 526.52 | 6.91 | 0.81 | 7.69 | 0.00 | 25.39 | 342.4 | 0.40
2024-03-11 | 2024-07-18 | 0.0 | 0.0 | 0.0 | N-4 | 121.42 | No | - | 472.92 | 6.70 | 0.73 | 7.72 | 0.53 | 25.96 | 263.0 | 0.36
2024-03-11 | 2024-08-08 | 0.0 | 0.0 | 0.0 | N-3 | 121.56 | No | - | 507.49 | 6.86 | 0.78 | 8.06 | 0.00 | 25.35 | 303.6 | 0.39
2024-03-11 | 2024-08-20 | 0.0 | 0.0 | 0.0 | N-3 | 122.09 | No | - | 506.33 | 6.75 | 0.78 | 7.66 | 0.06 | 25.53 | 380.8 | 0.39
2024-03-11 | 2024-09-06 | 0.0 | 0.0 | 0.0 | N-4 | 121.82 | No | - | 464.47 | 7.02 | 0.71 | 7.72 | 0.60 | 25.89 | 236.3 | 0.35
2024-03-11 | 2024-09-19 | 0.0 | 0.0 | 0.0 | 252094 | 121.41 | No | - | 483.52 | 6.91 | 0.74 | 7.64 | 0.30 | 25.72 | 288.3 | 0.37
2024-03-11 | 2024-10-03 | 0.0 | 0.0 | 0.0 | N-4 | 121.44 | No | - | 509.16 | 6.87 | 0.78 | 7.64 | 0.04 | 25.40 | 265.9 | 0.39
2024-03-11 | 2024-10-24 | 0.0 | 0.0 | 0.0 | N-3 | 121.38 | No | - | 482.27 | 7.05 | 0.74 | 7.69 | 0.32 | 25.24 | 169.5 | 0.37
2024-03-11 | 2024-11-07 | 0.0 | 0.0 | 0.0 | N-5 | 121.25 | No | - | 552.85 | 6.83 | 0.85 | 7.27 | 0.10 | 24.61 | 157.5 | 0.42
2024-03-11 | 2024-11-21 | 0.0 | 0.0 | 0.0 | N-5 | 121.12 | No | - | 484.96 | 6.83 | 0.75 | 7.59 | 0.22 | 24.51 | 163.2 | 0.37
2024-03-11 | 2024-12-05 | 0.0 | 0.0 | 0.0 | N-3 | 120.15 | No | - | 467.05 | 6.85 | 0.72 | 7.77 | 0.26 | 24.63 | 242.2 | 0.35
2024-03-11 | 2024-12-19 | 0.0 | 0.0 | 0.0 | N-4 | 121.22 | No | - | 488.94 | 6.78 | 0.75 | 7.66 | 0.00 | 24.58 | 304.7 | 0.37
| RHP03 Headspace and Product Gauging | [7 empty] | RHP03 Parameter Readings
WEEK | DATE | AMBIENT | TOP-OF-CASING HEADSPACE | GROUNDWATER HEADSPACE | TAPE | DTW (Raw) | PRODUCT? | THICKNESS | TDS | pH | Sp. Cond. | D.O. | Turbidity | TEMP | ORP | SAL
|  | (ppmv) | (ppmv) | (ppmv) | (Serial #) | (ft btoc) | (Yes/No) | (ft) | (ppm) |  | (mS/cm) | (mg/L) | (NTU) | (°C) | (Mv) | (psu)
06/12/2023 | 06/16/2023 | 0.0 | 0.0 | - | N-3 | 118.78 | No | - | 700.00 | 7.19 | 1.08 | 3.05 | 2.32 | 25.25 | x | 0.54
07/03/2023 | 07/03/2023 | 0.0 | 0.0 | - | N-3 | 119.12 | No | - | 643.15 | 7.31 | 0.99 | 3.46 | 4.06 | 25.78 | 157.5 | 0.49
07/31/2023 | 08/04/2023 | 0.0 | 0.0 | - | N-6 | 119.2 | No | - | 674.18 | 7.31 | 1.04 | 4.49 | 0.11 | 25.79 | 102.0 | 0.52
09/04/2023 | 09/08/2023 | 0.1 | 0.3 | - | N-3 | 119.33 | No | - | 719.65 | 7.18 | 1.11 | 4.68 | 0.00 | 25.73 | 114.1 | 0.56
10/02/2023 | 10/06/2023 | 0.0 | 0.0 | - | N-3 | 119.39 | No | - | 681.21 | 6.95 | 1.05 | 4.64 | 11.15 | 25.37 | 277.0 | 0.52
10/23/2023 | 10/26/2023 | 0.0 | 0.0 | - | N-3 | 119.45 | No | - | 722.52 | 7.33 | 1.11 | 4.40 | 0.20 | 25.44 | 271.3 | 0.56
10/30/2023 | 11/02/2023 | 0.0 | 0.0 | - | N-3 | 119.43 | No | - | 715.42 | 7.21 | 1.10 | 4.43 | 0.54 | 25.24 | 252.7 | 0.55
11/06/2023 | 11/08/2023 | 0.0 | 0.0 | - | N-5 | 119.46 | No | - | 683.81 | 7.29 | 1.10 | 4.50 | 0.36 | 24.64 | 219.5 | 0.53
2023-11-13 | 2023-11-14 | 0.0 | 0.0 | - | N-4 | 119.52 | No | - | 687.99 | 7.33 | 1.06 | 4.58 | 0.00 | 24.70 | 156.9 | 0.53
2023-11-20 | 2023-11-22 | 0.0 | 0.0 | - | N-5 | 119.48 | No | - | 669.79 | 7.29 | 1.03 | 4.67 | 0.00 | 24.39 | 254.7 | 0.52
2023-11-27 | 2023-11-27 | 0.0 | 0.0 | - | N-3 | 119.44 | No | - | 668.32 | 7.35 | 1.03 | 5.09 | 0.15 | 24.39 | 236.8 | 0.51
2023-12-04 | 2023-12-06 | 0.0 | 0.0 | - | N-3 | 119.34 | No | - | 694.93 | 7.29 | 1.07 | 4.78 | 0.12 | 24.47 | 171.0 | 0.54
2023-12-11 | 2023-12-11 | 0.0 | 0.0 | - | N-3 | 119.32 | No | - | 665.64 | 7.32 | 1.02 | 5.27 | 0.10 | 24.43 | 225.2 | 0.51
2023-12-18 | 2023-12-18 | 0.0 | 0.0 | - | N-3 | 119.31 | No | - | 684.56 | 7.39 | 1.05 | 4.91 | 0.13 | 23.93 | 192.3 | 0.53
2023-12-25 | 2023-12-26 | 0.0 | 0.0 | - | N-3 | 119.26 | No | - | 673.20 | 7.34 | 1.04 | 4.95 | 0.32 | 24.08 | 217.6 | 0.52
2024-01-01 | 2024-01-02 | 0.0 | 0.0 | - | N-5 | 119.28 | No | - | 673.54 | 7.36 | 1.04 | 5.01 | 0.00 | 24.35 | 274.0 | 0.52
2024-01-08 | 2024-01-08 | 0.0 | 0.0 | - | N-4 | 119.24 | No | - | 697.60 | 7.31 | 1.07 | 5.00 | 0.00 | 24.05 | 257.0 | 0.54
2024-01-15 | 2024-01-15 | 0.0 | 0.0 | - | N-4 | 119.17 | No | - | 696.93 | 7.29 | 1.07 | 4.89 | 0.22 | 24.04 | 168.8 | 0.54
2024-02-05 | 2024-02-08 | 0.0 | 0.0 | - | N-5 | 119.13 | No | - | 665.00 | 7.26 | 1.02 | 4.58 | 0.19 | 24.15 | 131.1 | 0.51
2024-03-11 | 2024-03-14 | 0.0 | 0.0 | - | N-5 | 119.13 | No | - | 656.54 | 7.29 | 1.01 | 4.67 | 0.11 | 24.68 | 271.1 | 0.50
2024-03-11 | 2024-04-04 | 0.0 | 0.0 | - | N-6 | 119.22 | No | - | 674.65 | 7.28 | 1.04 | 4.70 | 0.00 | 24.57 | 255.7 | 0.52
2024-03-11 | 2024-05-09 | 0.0 | 0.0 | 0.0 | N-5 | 118.91 | No | - | 704.70 | 7.36 | 1.08 | 4.61 | 0.35 | 24.43 | 260.2 | 0.54
2024-03-11 | 2024-05-23 | 0.0 | 0.0 | 0.0 | N-3 | 118.8 | No | - | 662.13 | 7.14 | 1.02 | 4.35 | 0.55 | 25.83 | 247.2 | 0.51
2024-03-11 | 2024-06-06 | 0.1 | 0.1 | 0.0 | N-5 | 118.81 | No | - | 709.24 | 7.40 | 1.09 | 4.03 | 0.74 | 26.95 | 257.7 | 0.55
2024-03-11 | 2024-06-20 | 0.0 | 0.0 | 0.0 | N-4 | 118.89 | No | - | 660.94 | 7.44 | 1.02 | 3.72 | 0.14 | 25.63 | 245.5 | 0.51
2024-03-11 | 2024-07-03 | 0.0 | 0.0 | 0.0 | N-5 | 118.87 | No | - | 720.20 | 7.40 | 1.11 | 3.72 | 0.00 | 24.63 | 292.8 | 0.56
2024-03-11 | 2024-07-18 | 0.0 | 0.0 | 0.0 | N-4 | 118.74 | No | - | 706.79 | 7.37 | 1.09 | 3.44 | 0.70 | 25.92 | 175.5 | 0.54
2024-03-11 | 2024-08-22 | 0.0 | 0.0 | 0.0 | N-3 | 118.71 | No | - | 755.83 | 7.41 | 1.16 | 3.00 | 0.02 | 25.39 | 278.2 | 0.58
2024-03-11 | 2024-09-09 | 0.0 | 0.0 | 0.0 | N-3 | 118.5 | No | - | 715.87 | 7.67 | 1.10 | 2.84 | 0.27 | 25.64 | 177.0 | 0.55
2024-03-11 | 2024-09-19 | 0.0 | 0.0 | 0.0 | 252094 | 118.55 | No | - | 761.13 | 7.23 | 1.17 | 3.66 | 0.10 | 25.41 | 235.1 | 0.59
2024-03-11 | 2024-10-09 | 0.0 | 0.0 | 0.0 | N-4 | 118.74 | No | - | 755.15 | 7.38 | 1.16 | 3.22 | 0.00 | 24.78 | 209.9 | 0.58
2024-03-11 | 2024-10-24 | 0.0 | 0.0 | 0.0 | N-4 | 118.57 | No | - | 731.08 | 7.35 | 1.12 | 3.40 | 0.36 | 25.10 | 139.6 | 0.56
2024-03-11 | 2024-11-07 | 0.0 | 0.0 | 0.0 | N-5 | 118.47 | No | - | 852.34 | 7.37 | 1.31 | 3.10 | 0.01 | 24.39 | 141.9 | 0.66
2024-03-11 | 2024-11-21 | 0.0 | 0.0 | 0.0 | N-5 | 118.35 | No | - | 769.07 | 7.37 | 1.18 | 2.97 | 0.26 | 24.72 | 108.1 | 0.60
2024-03-11 | 2024-12-05 | 0.0 | 0.0 | 0.0 | N-3 | 118.36 | No | - | 737.70 | 7.36 | 1.13 | 3.21 | 0.25 | 24.87 | 183.4 | 0.57
2024-03-11 | 2024-12-19 | 0.0 | 0.0 | 0.0 | N-4 | 118.43 | No | - | 763.88 | 7.32 | 1.18 | 3.19 | 0.00 | 24.77 | 255.5 | 0.59
| RHP04A Headspace and Product Gauging | [7 empty] | RHP04A Parameter Readings
WEEK | DATE | AMBIENT | TOP-OF-CASING HEADSPACE | GROUNDWATER HEADSPACE | TAPE | DTW (Raw) | PRODUCT? | THICKNESS | TDS | pH | Sp. Cond. | D.O. | Turbidity | TEMP | ORP | SAL
|  | (ppmv) | (ppmv) | (ppmv) | (Serial #) | (ft btoc) | (Yes/No) | (ft) | (ppm) |  | (mS/cm) | (mg/L) | (NTU) | (°C) | (Mv) | (psu)
06/12/2023 | 06/14/2023 | 0.0 | 0.0 | - | N-6 | 139.83 | No | - | 604.10 | 7.71 | 0.93 | 2.88 | 6.63 | 25.68 | 109.6 | 0.46
07/03/2023 | 07/03/2023 | 0.0 | 0.0 | - | N-6 | 140.1 | No | - | 602.08 | 7.55 | 0.93 | 2.27 | 9.26 | 26.71 | -131.7 | 0.46
08/07/2023 | 08/07/2023 | 0.0 | 0.0 | - | N-6 | 140.15 | No | - | 590.88 | 7.62 | 0.91 | 3.21 | 0.00 | 27.09 | 10.0 | 0.45
09/11/2023 | 09/11/2023 | 0.0 | 0.3 | - | N-6 | 140.33 | No | - | 625.53 | 7.44 | 0.96 | 3.56 | 8.38 | 26.69 | 68.8 | 0.48
10/02/2023 | 10/06/2023 | 0.0 | 0.0 | - | N-5 | 140.34 | No | - | 615.94 | 7.40 | 0.95 | 3.19 | 0.11 | 25.87 | 176.2 | 0.47
10/23/2023 | 10/23/2023 | 0.0 | 0.0 | - | N-6 | 140.1 | No | - | 601.92 | 7.38 | 0.93 | 3.51 | 0.00 | 26.52 | 193.4 | 0.46
10/30/2023 | 11/03/2023 | 0.0 | 0.1 | - | N-3 | 140.43 | No | - | 621.24 | 7.47 | 0.96 | 3.61 | 0.18 | 25.61 | 250.5 | 0.48
11/06/2023 | 11/07/2023 | 0.0 | 0.0 | - | N-3 | 140.4 | No | - | 612.25 | 7.50 | 0.90 | 3.60 | 0.12 | 25.89 | 172.7 | 0.47
2023-11-13 | 2023-11-15 | 0.0 | 0.0 | - | N-6 | 140.43 | No | - | 597.69 | 7.47 | 0.92 | 4.27 | 0.00 | 25.13 | 228.7 | 0.46
2023-11-20 | 2023-11-22 | 0.5 | 0.0 | - | N-3 | 140.41 | No | - | 612.74 | 7.43 | 0.94 | 3.68 | 0.31 | 26.12 | 170.8 | 0.47
2023-11-27 | 2023-11-28 | 0.0 | 0.0 | - | N-3 | 140.36 | No | - | 612.33 | 7.46 | 0.94 | 3.59 | 0.84 | 25.37 | 210.4 | 0.47
2023-12-04 | 2023-12-05 | 1.0 | 3.0 | - | N-3 | 140.27 | No | - | 601.96 | 7.46 | 0.93 | 3.84 | 0.07 | 25.29 | 181.7 | 0.46
2023-12-11 | 2023-12-12 | 0.0 | 0.0 | - | N-3 | 140.26 | No | - | 582.23 | 7.49 | 0.90 | 4.47 | 1.86 | 25.45 | 237.0 | 0.45
2023-12-18 | 2023-12-19 | 0.0 | 0.0 | - | N-3 | 140.29 | No | - | 608.06 | 7.50 | 0.94 | 3.66 | 9.49 | 24.96 | 222.0 | 0.47
2023-12-25 | 2023-12-27 | 0.0 | 0.0 | - | N-3 | 140.16 | No | - | 593.35 | 7.44 | 0.91 | 4.13 | 0.87 | 24.62 | 227.9 | 0.45
2024-01-01 | 2024-01-03 | 0.0 | 0.0 | - | N-5 | 140.17 | No | - | 629.29 | 7.45 | 0.97 | 3.73 | 4.91 | 26.39 | 191.8 | 0.48
2024-01-08 | 2024-01-09 | 0.0 | 0.0 | - | N-3 | 140.1 | No | - | 597.17 | 7.36 | 0.92 | 3.83 | 0.23 | 25.16 | 112.4 | 0.46
2024-01-15 | 2024-01-16 | 0.0 | 0.0 | - | N-6 | 140.08 | No | - | 617.02 | 7.20 | 0.95 | 4.23 | 1.36 | 25.64 | 228.6 | 0.47
2024-02-05 | 2024-02-09 | 0.0 | 0.0 | - | N-6 | 140.1 | No | - | 601.56 | 7.39 | 0.93 | 3.82 | 0.63 | 25.72 | 154.5 | 0.46
2024-03-11 | 2024-03-14 | 0.0 | 0.0 | - | N-5 | 140.09 | No | - | 655.52 | 7.16 | 1.01 | 3.69 | 0.00 | 25.57 | 226.9 | 0.50
2024-03-11 | 2024-04-04 | 0.0 | 0.0 | - | N-6 | 140.17 | No | - | 626.77 | 7.33 | 0.96 | 3.93 | 0.00 | 24.76 | 246.3 | 0.48
2024-03-11 | 2024-05-09 | 0.6 | 0.6 | 0.0 | N-5 | 139.87 | No | - | 631.70 | 7.37 | 0.97 | 3.89 | 0.41 | 25.27 | 260.3 | 0.48
2024-03-11 | 2024-05-23 | 0.0 | 0.0 | 0.0 | N-3 | 139.77 | No | - | 589.01 | 7.05 | 0.91 | 3.81 | 0.71 | 27.08 | 199.3 | 0.45
2024-03-11 | 2024-06-06 | 0.0 | 0.1 | 0.0 | N-5 | 139.77 | No | - | 622.67 | 7.36 | 0.96 | 3.64 | 4.53 | 26.67 | 251.0 | 0.48
2024-03-11 | 2024-06-20 | 0.0 | 0.0 | 0.0 | N-4 | 139.87 | No | - | 580.94 | 7.35 | 0.89 | 3.71 | 0.05 | 25.74 | 267.4 | 0.44
2024-03-11 | 2024-07-03 | 0.0 | 0.0 | 0.0 | N-5 | 139.82 | No | - | 646.09 | 7.33 | 0.99 | 3.89 | 0.00 | 26.02 | 308.2 | 0.50
2024-03-11 | 2024-07-18 | 0.0 | 0.0 | 0.0 | N-4 | 139.72 | No | - | 610.63 | 7.31 | 0.94 | 3.78 | 0.57 | 26.05 | 168.9 | 0.47
2024-03-11 | 2024-08-22 | 0.0 | 0.0 | 0.0 | N-3 | 139.64 | No | - | 646.43 | 7.32 | 1.01 | 4.24 | 0.55 | 27.83 | 289.4 | 0.50
2024-03-11 | 2024-09-09 | 0.0 | 0.1 | 0.0 | N-3 | 139.41 | No | - | 596.97 | 7.70 | 0.92 | 3.67 | 0.60 | 26.35 | 138.3 | 0.46
2024-03-11 | 2024-09-17 | 0.0 | 0.0 | 0.0 | 252094 | 139.65 | No | - | 618.85 | 7.41 | 0.95 | 3.81 | 0.10 | 26.68 | 213.9 | 0.47
2024-03-11 | 2024-10-09 | 0.0 | 0.0 | 0.0 | N-4 | 139.65 | No | - | 647.65 | 7.50 | 1.00 | 2.55 | 0.00 | 25.97 | 226.2 | 0.50
2024-03-11 | 2024-10-24 | 0.0 | 0.0 | 0.0 | N-5 | 139.5 | No | - | 650.64 | 7.40 | 1.00 | 3.07 | 0.17 | 26.21 | 98.0 | 0.50
2024-03-11 | 2024-11-07 | 0.0 | 0.0 | 0.0 | N-3 | 139.42 | No | - | 631.62 | 7.34 | 0.97 | 3.51 | 0.00 | 25.20 | 68.1 | 0.48
2024-03-11 | 2024-11-21 | 0.0 | 0.0 | 0.0 | N-3 | 139.29 | No | - | 601.02 | 7.43 | 0.92 | 3.60 | 3.25 | 25.86 | 201.3 | 0.46
2024-03-11 | 2024-12-05 | 0.0 | 0.0 | 0.0 | N-3 | 139.37 | No | - | 623.44 | 7.31 | 0.96 | 3.68 | 0.14 | 25.39 | 164.4 | 0.48
2024-03-11 | 2024-12-19 | 0.0 | 0.0 | 0.0 | N-4 | 139.41 | No | - | 622.09 | 7.26 | 0.96 | 3.69 | 0.00 | 25.19 | 248.2 | 0.48
| RHP04B Headspace and Product Gauging | [7 empty] | RHP04B Parameter Readings
WEEK | DATE | AMBIENT | TOP-OF-CASING HEADSPACE | GROUNDWATER HEADSPACE | TAPE | DTW (Raw) | PRODUCT? | THICKNESS | TDS | pH | Sp. Cond. | D.O. | Turbidity | TEMP | ORP | SAL
|  | (ppmv) | (ppmv) | (ppmv) | (Serial #) | (ft btoc) | (Yes/No) | (ft) | (ppm) |  | (mS/cm) | (mg/L) | (NTU) | (°C) | (Mv) | (psu)
06/12/2023 | 06/14/2023 | 0.0 | 0.0 | - | N-6 | 138.95 | No | - | 448.12 | 7.80 | 0.69 | 0.97 | 0.26 | 25.72 | -337.2 | 0.34
07/03/2023 | 07/03/2023 | 0.0 | 0.0 | - | N-6 | 139.23 | No | - | 447.81 | 7.71 | 0.69 | 0.65 | 1.24 | 26.62 | -279.0 | 0.34
08/07/2023 | 08/07/2023 | 0.0 | 0.0 | - | N-6 | 139.27 | No | - | 412.10 | 7.87 | 0.63 | 0.43 | 0.00 | 25.56 | -334.5 | 0.31
09/11/2023 | 09/11/2023 | 0.0 | 0.6 | - | N-6 | 139.45 | No | - | 418.31 | 7.78 | 0.64 | 0.38 | 0.00 | 25.44 | -372.4 | 0.32
10/02/2023 | 10/06/2023 | 0.0 | 0.3 | - | N-5 | 139.48 | No | - | 421.42 | 7.86 | 0.65 | 0.15 | 0.20 | 25.89 | -197.7 | 0.32
10/23/2023 | 10/23/2023 | 0.1 | 0.0 | - | N-6 | 139.57 | No | - | 386.10 | 7.76 | 0.59 | 0.18 | 0.00 | 26.01 | -207.5 | 0.29
10/30/2023 | 11/03/2023 | 0.0 | 0.2 | - | N-3 | 139.5 | No | - | 398.58 | 7.89 | 0.61 | 0.17 | 0.33 | 26.03 | -185.3 | 0.30
11/06/2023 | 11/07/2023 | 0.0 | 0.0 | - | N-3 | 139.52 | No | - | 388.14 | 7.93 | 0.60 | 0.20 | 0.08 | 25.70 | -174.5 | 0.29
2023-11-13 | 2023-11-15 | 0.3 | 0.2 | - | N-6 | 139.57 | No | - | 381.94 | 7.91 | 0.59 | 0.20 | 0.00 | 25.50 | -158.0 | 0.29
2023-11-20 | 2023-11-22 | 0.5 | 0.0 | - | N-3 | 139.54 | No | - | 388.23 | 7.87 | 0.60 | 0.16 | 0.79 | 25.28 | -119.7 | 0.29
2023-11-27 | 2023-11-28 | 0.0 | 0.1 | - | N-3 | 139.43 | No | - | 384.67 | 7.93 | 0.59 | 0.18 | 0.77 | 25.28 | -73.4 | 0.29
2023-12-04 | 2023-12-05 | 0.3 | 0.4 | - | N-3 | 139.4 | No | - | 375.65 | 7.94 | 0.58 | 0.15 | 0.08 | 25.03 | -122.2 | 0.28
2023-12-11 | 2023-12-12 | 0.0 | 0.0 | - | N-3 | 139.34 | No | - | 362.19 | 7.96 | 0.56 | 0.15 | 0.00 | 24.96 | -140.1 | 0.27
2023-12-18 | 2023-12-19 | 0.0 | 0.0 | - | N-3 | 139.36 | No | - | 377.32 | 8.06 | 0.58 | 0.19 | 0.28 | 25.21 | -118.0 | 0.28
2023-12-25 | 2023-12-27 | 0.0 | 0.0 | - | N-3 | 139.27 | No | - | 366.93 | 8.00 | 0.56 | 0.20 | 0.93 | 25.64 | -83.2 | 0.28
2024-01-01 | 2024-01-03 | 0.0 | 0.0 | - | N-5 | 139.29 | No | - | 391.20 | 8.01 | 0.60 | 0.28 | 0.00 | 25.80 | -97.3 | 0.29
2024-01-08 | 2024-01-09 | 0.0 | 0.0 | - | N-3 | 139.23 | No | - | 368.26 | 7.96 | 0.57 | 0.15 | 0.06 | 25.40 | -215.7 | 0.28
2024-01-15 | 2024-01-16 | 0.0 | 4.5 | - | N-3 | 139.19 | No | - | 373.46 | 7.95 | 0.57 | 0.24 | 0.00 | 25.49 | -58.7 | 0.28
2024-02-12 | 2024-02-14 | 0.0 | 0.0 | - | N-5 | 139.11 | No | - | 381.45 | 7.92 | 0.59 | 0.22 | 0.42 | 25.19 | -160.7 | 0.29
2024-02-12 | 2024-03-19 | 0.0 | 0.0 | - | N-4 | 139.23 | No | - | 376.88 | 7.97 | 0.58 | 0.19 | 0.29 | 25.38 | -221.8 | 0.28
2024-03-18 | 2024-04-09 | 0.0 | 0.0 | - | N-6 | 139.26 | No | - | 381.78 | 7.94 | 0.59 | 0.17 | 0.18 | 25.25 | -124.8 | 0.29
2024-03-18 | 2024-05-14 | 0.0 | 0.1 | - | N-5 | 139.37 | No | - | 353.41 | 7.93 | 0.54 | 0.20 | 0.73 | 25.83 | -92.3 | 0.27
2024-03-18 | 2024-05-28 | 0.0 | 0.0 | - | N-3 | 138.69 | No | - | 371.44 | 7.97 | 0.57 | 0.14 | 0.14 | 26.00 | -97.4 | 0.28
2024-03-18 | 2024-06-11 | 0.0 | 0.0 | - | N-3 | 138.88 | No | - | 343.52 | 7.98 | 0.53 | 0.20 | 0.14 | 26.36 | -129.6 | 0.26
2024-03-18 | 2024-06-25 | 0.0 | 0.0 | - | N-4 | 138.91 | No | - | 375.41 | 7.98 | 0.58 | 0.19 | 0.00 | 25.48 | -43.6 | 0.28
2024-03-18 | 2024-07-09 | 0.0 | 0.0 | - | N-5 | 138.89 | No | - | 350.83 | 7.95 | 0.54 | 0.28 | 0.01 | 26.62 | -101.4 | 0.26
2024-03-18 | 2024-07-23 | 0.0 | 0.0 | - | N-4 | 138.95 | No | - | 340.42 | 8.04 | 0.52 | 0.23 | 0.11 | 26.84 | -43.5 | 0.26
2024-03-18 | 2024-08-13 | 0.0 | 0.0 | - | N-4 | 138.81 | No | - | 348.91 | 8.05 | 0.54 | 0.20 | 0.07 | 26.03 | -46.8 | 0.26
2024-03-18 | 2024-08-27 | 0.0 | 0.0 | - | N-3 | 138.82 | No | - | 358.34 | 8.02 | 0.55 | 0.20 | 0.83 | 26.51 | -47.0 | 0.27
2024-03-18 | 2024-09-11 | 0.0 | 0.0 | - | 252094 | 138.69 | No | - | 379.08 | 7.98 | 0.58 | 0.16 | 0.00 | 26.80 | 40.0 | 0.29
2024-03-18 | 2024-09-24 | 0.0 | 0.0 | - | N-4 | 138.73 | No | - | 350.78 | 8.01 | 0.54 | 0.22 | 0.59 | 26.77 | -22.0 | 0.26
2024-03-18 | 2024-10-15 | 0.0 | 0.0 | - | N-3 | 138.58 | No | - | 382.00 | 8.06 | 0.59 | 0.22 | 0.38 | 25.84 | -98.6 | 0.29
2024-03-18 | 2024-10-29 | 0.0 | 0.0 | - | N-5 | 138.72 | No | - | 363.48 | 7.93 | 0.56 | 0.17 | 0.03 | 25.59 | -217.1 | 0.27
2024-03-18 | 2024-11-11 | 0.0 | 0.0 | - | N-4 | 138.48 | No | - | 369.53 | 7.97 | 0.57 | 0.21 | 0.26 | 25.44 | -226.8 | 0.28
2024-03-18 | 2024-11-26 | 0.0 | 0.0 | - | N-3 | 138.58 | No | - | 358.75 | 7.92 | 0.55 | 0.21 | 0.39 | 25.29 | -262.1 | 0.27
2024-03-18 | 2024-12-10 | 0.0 | 0.0 | - | N-4 | 138.46 | No | - | 356.34 | 7.99 | 0.55 | 0.19 | 0.20 | 25.33 | -72.0 | 0.27
2024-03-18 | 2024-12-26 | 0.0 | 0.0 | - | N-5 | 138.49 | No | - | 367.45 | 7.95 | 0.57 | 0.16 | 0.57 | 25.65 | -76.9 | 0.28
| RHP04C Headspace and Product Gauging | [7 empty] | RHP04C Parameter Readings
WEEK | DATE | AMBIENT | TOP-OF-CASING HEADSPACE | GROUNDWATER HEADSPACE | TAPE | DTW (Raw) | PRODUCT? | THICKNESS | TDS | pH | Sp. Cond. | D.O. | Turbidity | TEMP | ORP | SAL
|  | (ppmv) | (ppmv) | (ppmv) | (Serial #) | (ft btoc) | (Yes/No) | (ft) | (ppm) |  | (mS/cm) | (mg/L) | (NTU) | (°C) | (Mv) | (psu)
06/12/2023 | 06/16/2023 | 0.1 | 8.9 | - | N-6 | 138.17 | No | - | 1016.94 | 7.45 | 1.56 | 0.63 | 0.32 | 26.99 | -96.1 | 0.80
07/03/2023 | 07/03/2023 | 0.0 | 2.6 | - | N-6 | 138.5 | No | - | 895.19 | 7.49 | 1.38 | 0.83 | 0.05 | 27.02 | 121.7 | 0.70
07/31/2023 | 08/04/2023 | 0.0 | 2.7 | - | N-6 | 138.54 | No | - | 891.84 | 7.44 | 1.37 | 0.80 | 0.00 | 26.01 | 51.3 | 0.69
09/04/2023 | 09/08/2023 | 0.2 | 5.3 | - | N-3 | 138.66 | No | - | 946.67 | 7.28 | 1.46 | 1.01 | 0.00 | 26.20 | 32.9 | 0.74
10/02/2023 | 10/06/2023 | 0.0 | 0.0 | - | N-3 | 138.73 | No | - | 859.21 | 7.36 | 1.32 | 4.18 | 0.94 | 26.15 | 258.2 | 0.67
10/23/2023 | 10/25/2023 | 0.0 | 0.0 | - | N-3 | 138.79 | No | - | 907.76 | 7.50 | 1.40 | 1.92 | 0.18 | 26.29 | 71.2 | 0.71
10/30/2023 | 11/01/2023 | 0.0 | 0.0 | - | N-4 | 138.8 | No | - | 880.18 | 7.53 | 1.35 | 1.48 | 0.02 | 26.04 | 194.5 | 0.69
11/06/2023 | 11/06/2023 | 0.0 | 0.5 | - | N-3 | 138.83 | No | - | 907.23 | 7.55 | 1.40 | 1.40 | 0.00 | 25.71 | 199.0 | 0.71
2023-11-13 | 2023-11-15 | 0.0 | 0.0 | - | N-3 | 138.81 | No | - | 909.76 | 7.54 | 1.40 | 1.11 | 0.21 | 25.26 | 194.4 | 0.71
2023-11-20 | 2023-11-20 | 0.0 | 0.0 | - | N-4 | 138.87 | No | - | 889.17 | 7.51 | 1.37 | 1.28 | 0.58 | 25.58 | 190.3 | 0.69
2023-11-27 | 2023-11-29 | 0.0 | 0.1 | - | N-5 | 138.72 | No | - | 891.11 | 7.49 | 1.37 | 0.68 | 0.05 | 25.20 | 160.3 | 0.69
2023-12-04 | 2023-12-04 | 0.0 | 0.2 | - | N-6 | 138.73 | No | - | 878.97 | 7.58 | 1.35 | 1.09 | 0.94 | 26.11 | 160.3 | 0.68
2023-12-11 | 2023-12-13 | 0.0 | 0.0 | - | N-3 | 138.69 | No | - | 891.98 | 7.48 | 1.37 | 0.97 | 0.00 | 25.56 | 183.5 | 0.69
2023-12-18 | 2023-12-20 | 0.0 | 0.0 | - | N-4 | 138.69 | No | - | 895.07 | 7.49 | 1.38 | 0.83 | 0.14 | 25.04 | 181.0 | 0.70
2023-12-25 | 2023-12-28 | 0.0 | 0.1 | - | N-3 | 138.57 | No | - | 922.44 | 7.52 | 1.42 | 0.81 | 0.28 | 25.00 | 204.6 | 0.72
2024-01-01 | 2024-01-05 | 0.0 | 0.1 | - | N-5 | 138.58 | No | - | 915.63 | 7.40 | 1.41 | 0.74 | 0.65 | 25.84 | 206.9 | 0.71
2024-01-08 | 2024-01-10 | 0.0 | 0.0 | - | N-4 | 138.57 | No | - | 935.26 | 7.48 | 1.44 | 0.97 | 0.32 | 25.13 | 198.6 | 0.73
2024-01-15 | 2024-01-17 | 0.0 | 0.1 | - | N-5 | 138.48 | No | - | 898.89 | 7.49 | 1.38 | 1.11 | 1.29 | 24.84 | 191.9 | 0.70
2024-02-12 | 2024-02-14 | 0.0 | 0.0 | - | N-5 | 138.42 | No | - | 948.27 | 7.48 | 1.46 | 0.55 | 0.27 | 25.01 | 86.8 | 0.74
2024-03-18 | 2024-03-19 | 0.0 | 0.0 | - | N-4 | 138.51 | No | - | 921.16 | 7.51 | 1.42 | 0.40 | 0.24 | 25.31 | 74.5 | 0.72
2024-03-18 | 2024-04-09 | 0.0 | 0.0 | - | N-6 | 138.57 | No | - | 937.31 | 7.49 | 1.44 | 0.37 | 0.26 | 25.69 | 115.4 | 0.73
2024-03-18 | 2024-05-14 | 0.0 | 0.2 | - | N-5 | 138.37 | No | - | 883.85 | 7.43 | 1.36 | 0.59 | 0.61 | 25.75 | 111.5 | 0.69
2024-03-18 | 2024-05-28 | 0.1 | 0.0 | - | N-3 | 138.01 | No | - | 908.20 | 7.46 | 1.40 | 0.72 | 0.37 | 26.61 | 142.6 | 0.71
2024-03-18 | 2024-06-11 | 0.0 | 0.0 | - | N-4 | 138.2 | No | - | 871.72 | 7.39 | 1.34 | 0.76 | 0.42 | 26.19 | 151.8 | 0.68
2024-03-18 | 2024-06-25 | 0.0 | 0.0 | - | N-4 | 138.22 | No | - | 924.12 | 7.40 | 1.42 | 0.84 | 0.19 | 27.82 | 186.0 | 0.72
2024-03-18 | 2024-07-09 | 0.0 | 0.0 | - | N-4 | 138.2 | No | - | 914.31 | 7.45 | 1.41 | 0.62 | 0.00 | 25.93 | 164.5 | 0.71
2024-03-18 | 2024-07-23 | 0.0 | 0.0 | - | N-3 | 138.2 | No | - | 852.90 | 7.52 | 1.31 | 0.68 | 0.00 | 26.00 | 94.5 | 0.66
2024-03-18 | 2024-08-13 | 0.0 | 0.0 | - | N-4 | 138.15 | No | - | 877.11 | 7.44 | 1.35 | 0.76 | 0.32 | 27.93 | 105.5 | 0.68
2024-03-18 | 2024-08-27 | 0.0 | 0.0 | - | N-3 | 138.08 | No | - | 900.24 | 7.45 | 1.38 | 0.64 | 0.94 | 27.82 | 99.7 | 0.70
2024-03-18 | 2024-09-11 | 0.0 | 0.0 | - | 252094 | 138 | No | - | 923.02 | 7.38 | 1.42 | 0.56 | 0.39 | 27.08 | 179.2 | 0.72
2024-03-18 | 2024-09-24 | 0.0 | 0.0 | - | N-4 | 138.04 | No | - | 858.79 | 7.48 | 1.32 | 0.75 | 0.26 | 26.38 | 124.3 | 0.67
2024-03-18 | 2024-10-15 | 0.0 | 0.0 | - | N-3 | 137.9 | No | - | 934.97 | 7.50 | 1.44 | 0.90 | 4.76 | 26.77 | 171.2 | 0.73
2024-03-18 | 2024-10-29 | 0.0 | 0.0 | - | N-4 | 138.03 | No | - | 840.05 | 7.57 | 1.29 | 0.73 | 0.00 | 25.78 | -1.0 | 0.65
2024-03-18 | 2024-11-11 | 0.0 | 0.0 | - | N-3 | 138.48 | No | - | 915.39 | 7.40 | 1.41 | 0.99 | 0.00 | 26.42 | 136.8 | 0.71
2024-03-18 | 2024-11-26 | 0.0 | 0.0 | - | N-3 | 137.86 | No | - | 901.06 | 7.40 | 1.39 | 0.78 | 0.46 | 25.51 | -17.7 | 0.70
2024-03-18 | 2024-12-10 | 0.0 | 0.0 | - | N-4 | 137.8 | No | - | 905.72 | 7.45 | 1.39 | 0.75 | 0.21 | 25.34 | 201.7 | 0.71
2024-03-18 | 2024-12-26 | 0.0 | 0.0 | - | N-5 | 137.75 | No | - | 905.84 | 7.35 | 1.39 | 0.87 | 0.55 | 25.66 | 102.0 | 0.71
| RHP05 Headspace and Product Gauging | [7 empty] | RHP05 Parameter Readings
WEEK | DATE | AMBIENT | TOP-OF-CASING HEADSPACE | GROUNDWATER HEADSPACE | TAPE | DTW (Raw) | PRODUCT? | THICKNESS | TDS | pH | Sp. Cond. | D.O. | Turbidity | TEMP | ORP | SAL
|  | (ppmv) | (ppmv) | (ppmv) | (Serial #) | (ft btoc) | (Yes/No) | (ft) | (ppm) |  | (mS/cm) | (mg/L) | (NTU) | (°C) | (Mv) | (psu)
06/12/2023 | 06/16/2023 | 0.0 | 0.0 | - | N-3 | 212.43 | No | - | 615.70 | 7.33 | 0.95 | 6.21 | 6.24 | 26.44 | 90.4 | 0.47
07/03/2023 | 07/06/2023 | 0.0 | 0.0 | - | N-4 | 212.92 | No | - | 576.85 | 7.42 | 0.89 | 4.72 | 0.44 | 26.90 | 140.8 | 0.44
07/31/2023 | 08/02/2023 | 0.0 | 0.0 | - | N-3 | 212.94 | No | - | 612.45 | 7.25 | 0.94 | 6.15 | 3.47 | 29.61 | 92.5 | 0.47
09/04/2023 | 09/08/2023 | 0.0 | 0.0 | - | N-4 | 213.09 | No | - | 615.30 | 7.17 | 0.95 | 6.14 | 0.00 | 27.71 | 115.2 | 0.47
10/02/2023 | 10/02/2023 | 0.0 | 0.0 | - | N-4 | 213.15 | No | - | 692.05 | 7.14 | 1.06 | 6.89 | 0.09 | 28.11 | 134.2 | 0.53
10/23/2023 | 10/26/2023 | 0.0 | 0.0 | - | N-3 | 213.18 | No | - | 658.25 | 7.27 | 1.01 | 6.65 | 0.19 | 26.39 | 275.5 | 0.51
10/30/2023 | 11/02/2023 | 0.0 | 0.0 | - | N-3 | 213.17 | No | - | 645.18 | 7.30 | 0.99 | 6.70 | 0.51 | 26.50 | 261.0 | 0.50
11/06/2023 | 11/08/2023 | 0.0 | 0.0 | - | N-4 | 213.26 | No | - | 638.93 | 7.25 | 1.00 | 6.80 | 0.00 | 25.45 | 298.5 | 0.49
2023-11-13 | 2023-11-15 | 0.0 | 0.3 | - | N-5 | 213.26 | No | - | 618.44 | 7.23 | 0.95 | 6.62 | 0.86 | 25.45 | 154.2 | 0.47
2023-11-20 | 2023-11-22 | 0.0 | 0.0 | - | N-6 | 213.25 | No | - | 618.04 | 7.25 | 0.95 | 6.58 | 0.33 | 25.50 | 258.1 | 0.47
2023-11-27 | 2023-11-29 | 0.0 | 0.0 | - | N-6 | 213.15 | No | - | 599.19 | 7.28 | 0.92 | 7.04 | 0.06 | 26.01 | 261.4 | 0.46
2023-12-04 | 2023-12-06 | 0.0 | 0.0 | - | N-4 | 213.11 | No | - | 603.75 | 7.29 | 0.93 | 6.64 | 4.48 | 26.39 | 254.1 | 0.46
2023-12-11 | 2023-12-13 | 0.0 | 0.0 | - | N-4 | 213.11 | No | - | 615.79 | 7.31 | 0.95 | 6.56 | 0.00 | 25.64 | 257.7 | 0.47
2023-12-18 | 2023-12-20 | 0.0 | 0.0 | - | N-5 | 213.04 | No | - | 626.44 | 7.27 | 0.96 | 6.70 | 0.00 | 25.16 | 217.6 | 0.48
2023-12-25 | 2023-12-28 | 0.0 | 0.0 | - | N-5 | 212.97 | No | - | 614.24 | 7.26 | 0.94 | 6.74 | 0.38 | 25.00 | 292.6 | 0.47
2024-01-01 | 2024-01-03 | 0.0 | 0.0 | - | N-3 | 212.9 | No | - | 627.79 | 7.12 | 0.97 | 7.37 | 3.62 | 26.61 | 261.4 | 0.48
2024-01-08 | 2024-01-10 | 0.0 | 0.0 | - | N-6 | 212.9 | No | - | 628.12 | 6.94 | 0.97 | 6.81 | 0.77 | 25.33 | 276.8 | 0.48
2024-01-15 | 2024-01-17 | 0.0 | 0.0 | - | N-6 | 212.94 | No | - | 623.00 | 7.25 | 0.96 | 6.69 | 0.28 | 25.58 | 215.9 | 0.48
2024-02-05 | 2024-02-08 | 0.0 | 0.0 | - | N-6 | 212.87 | No | - | 612.94 | 7.23 | 0.94 | 6.32 | 0.24 | 25.30 | 197.4 | 0.47
2024-03-11 | 2024-03-14 | 0.0 | 0.1 | - | N-5 | 212.86 | No | - | 607.76 | 7.22 | 0.94 | 6.35 | 1.12 | 25.57 | 289.1 | 0.47
2024-03-11 | 2024-04-05 | 0.0 | 0.1 | - | N-5 | 212.95 | No | - | 593.36 | 7.13 | 0.91 | 6.18 | 0.75 | 25.79 | 252.7 | 0.45
2024-03-11 | 2024-05-10 | 0.0 | 0.0 | 0.0 | N-5 | 212.58 | No | - | 636.66 | 7.14 | 0.98 | 6.19 | 0.43 | 25.26 | 293.2 | 0.49
2024-03-11 | 2024-05-24 | 0.0 | 0.0 | 0.0 | N-3 | 212.53 | No | - | 597.11 | 7.16 | 0.92 | 6.30 | 0.47 | 26.74 | 232.0 | 0.46
2024-03-11 | 2024-06-07 | 0.0 | 0.0 | 0.0 | N-4 | 212.42 | No | - | 636.85 | 7.16 | 0.98 | 6.23 | 0.41 | 26.77 | 282.1 | 0.49
2024-03-11 | 2024-06-21 | 0.0 | 0.0 | 0.0 | N-4 | 212.47 | No | - | 594.87 | 7.14 | 0.92 | 6.37 | 0.00 | 26.31 | 273.3 | 0.46
2024-03-11 | 2024-07-03 | 0.0 | 0.0 | 0.0 | N-5 | 212.52 | No | - | 650.48 | 7.20 | 1.00 | 6.42 | 0.00 | 27.26 | 333.6 | 0.50
2024-03-11 | 2024-07-19 | 0.0 | 0.0 | 0.0 | N-4 | 212.47 | No | - | 639.77 | 7.22 | 0.98 | 6.31 | 0.00 | 25.87 | 265.1 | 0.49
2024-03-11 | 2024-08-09 | 0.0 | 0.0 | 0.0 | N-5 | 212.37 | No | - | 596.53 | 7.22 | 0.92 | 6.41 | 0.08 | 26.44 | 205.0 | 0.46
2024-03-11 | 2024-08-23 | 0.0 | 0.0 | 0.0 | N-5 | 212.43 | No | - | 594.08 | 7.24 | 0.91 | 6.46 | 0.09 | 26.21 | 353.1 | 0.45
2024-03-11 | 2024-09-09 | 0.0 | 0.0 | 0.0 | N-5 | 212.23 | No | - | 599.97 | 7.27 | 0.92 | 6.49 | 1.35 | 27.66 | 258.6 | 0.46
2024-03-11 | 2024-09-17 | 0.0 | 0.0 | 0.0 | 288404 | 212.43 | No | - | 652.06 | 7.24 | 1.00 | 6.52 | 0.00 | 26.85 | 295.9 | 0.50
2024-03-11 | 2024-10-10 | 0.0 | 0.0 | 0.0 | N-4 | 212.32 | No | - | 590.93 | 7.14 | 0.91 | 6.51 | 0.22 | 26.53 | 210.0 | 0.45
2024-03-11 | 2024-10-25 | 0.0 | 0.0 | 0.0 | N-5 | 212.24 | No | - | 607.09 | 7.18 | 0.93 | 6.38 | 4.16 | 26.27 | 167.3 | 0.47
2024-03-11 | 2024-11-08 | 0.0 | 0.0 | 0.0 | N-5 | 212.15 | No | - | 591.56 | 7.27 | 0.91 | 6.27 | 0.43 | 25.87 | 134.0 | 0.45
2024-03-11 | 2024-11-19 | 0.0 | 0.0 | 0.0 | N-5 | 212.2 | No | - | 612.46 | 7.25 | 0.94 | 6.63 | 0.03 | 26.12 | 142.9 | 0.47
2024-03-11 | 2024-12-03 | 0.0 | 0.0 | 0.0 | N-3 | 212.08 | No | - | 612.04 | 7.08 | 0.94 | 6.40 | 0.76 | 26.10 | 231.3 | 0.47
2024-03-11 | 2024-12-17 | 0.0 | 0.0 | 0.0 | N-5 | 212.11 | No | - | 635.73 | 7.16 | 0.98 | 6.44 | 2.86 | 25.49 | 209.5 | 0.49
| RHP06 Headspace and Product Gauging | [7 empty] | RHP06 Parameter Readings
WEEK | DATE | AMBIENT | TOP-OF-CASING HEADSPACE | GROUNDWATER HEADSPACE | TAPE | DTW (Raw) | PRODUCT? | THICKNESS | TDS | pH | Sp. Cond. | D.O. | Turbidity | TEMP | ORP | SAL
|  | (ppmv) | (ppmv) | (ppmv) | (Serial #) | (ft btoc) | (Yes/No) | (ft) | (ppm) |  | (mS/cm) | (mg/L) | (NTU) | (°C) | (Mv) | (psu)
07/24/2023 | 07/24/2023 | 0.0 | 0.0 | - | N-5 | 253.33 | No | - | 688.87 | 7.50 | 1.06 | 6.06 | 13.59 | 26.96 | 73.2 | 0.53
07/31/2023 | 08/03/2023 | 0.0 | 0.7 | - | N-6 | 253.39 | No | - | 697.52 | 7.64 | 1.07 | 6.44 | 3.57 | 26.09 | 103.2 | 0.54
09/04/2023 | 09/07/2023 | 0.0 | 0.1 | - | N-6 | 253.55 | No | - | 713.26 | 6.99 | 1.10 | 6.93 | 0.69 | 25.96 | 111.9 | 0.55
10/02/2023 | 10/02/2023 | 0.0 | 0.0 | - | N-4 | 253.61 | No | - | 772.76 | 7.16 | 1.19 | 7.05 | 1.48 | 26.26 | 122.2 | 0.60
10/23/2023 | 10/27/2023 | 0.0 | 0.2 | - | N-3 | 253.6 | No | - | 724.18 | 7.20 | 1.11 | 7.15 | 0.60 | 25.99 | 305.0 | 0.56
10/30/2023 | 11/02/2023 | 0.0 | 0.0 | - | N-4 | 253.66 | No | - | 688.57 | 7.06 | 1.06 | 7.18 | 0.26 | 25.93 | 276.7 | 0.53
11/06/2023 | 11/08/2023 | 0.0 | 0.0 | - | N-4 | 253.69 | No | - | 718.52 | 7.08 | 1.10 | 7.60 | 1.80 | 25.92 | 312.7 | 0.55
2023-11-13 | 2023-11-15 | 0.0 | 44.1 | - | N-5 | 253.65 | No | - | 695.34 | 7.21 | 1.07 | 7.08 | 0.80 | 25.82 | 160.0 | 0.54
2023-11-20 | 2023-11-22 | 0.0 | 0.0 | - | N-6 | 253.69 | No | - | 696.69 | 7.13 | 1.07 | 7.15 | 0.36 | 25.52 | 277.1 | 0.54
2023-11-27 | 2023-11-29 | 0.0 | 0.0 | - | N-6 | 253.61 | No | - | 661.39 | 7.05 | 1.02 | 7.38 | 0.00 | 25.35 | 275.3 | 0.51
2023-12-04 | 2023-12-06 | 0.0 | 0.0 | - | N-4 | 253.59 | No | - | 679.64 | 7.51 | 1.05 | 7.31 | 0.38 | 25.39 | 248.8 | 0.52
2023-12-11 | 2023-12-13 | 0.0 | 0.0 | - | N-4 | 253.56 | No | - | 685.74 | 7.41 | 1.05 | 7.19 | 1.61 | 25.88 | 260.3 | 0.53
2023-12-18 | 2023-12-20 | 0.0 | 0.0 | - | N-5 | 253.43 | No | - | 679.56 | 7.05 | 1.05 | 7.25 | 0.00 | 25.03 | 270.9 | 0.52
2023-12-25 | 2023-12-28 | 0.0 | 0.0 | - | N-5 | 253.43 | No | - | 646.75 | 7.01 | 0.99 | 7.18 | 0.78 | 25.42 | 315.8 | 0.50
2024-01-01 | 2024-01-02 | 0.0 | 0.4 | - | N-3 | 253.4 | No | - | 656.95 | 7.05 | 1.01 | 7.16 | 0.29 | 25.85 | 278.3 | 0.50
2024-01-08 | 2024-01-08 | 0.3 | 0.5 | - | N-5 | 253.39 | No | - | 675.31 | 6.97 | 1.04 | 7.62 | 0.00 | 25.22 | 245.1 | 0.52
2024-01-15 | 2024-01-17 | 0.0 | 0.0 | - | N-6 | 253.39 | No | - | 657.48 | 7.16 | 1.01 | 7.19 | 0.80 | 25.24 | 267.7 | 0.51
2024-02-05 | 2024-02-08 | 0.0 | 0.0 | - | N-6 | 253.35 | No | - | 647.96 | 7.01 | 1.00 | 7.21 | 0.40 | 25.57 | 192.1 | 0.50
2024-03-11 | 2024-03-14 | 0.0 | 0.0 | - | N-5 | 253.3 | No | - | 641.39 | 7.05 | 0.99 | 7.31 | 1.07 | 25.62 | 295.5 | 0.49
2024-03-11 | 2024-04-05 | 0.0 | 1.1 | - | N-5 | 253.4 | No | - | 617.16 | 6.90 | 0.95 | 7.28 | 0.59 | 24.81 | 228.2 | 0.47
2024-03-11 | 2024-05-10 | 1.2 | 0.8 | 0.0 | N-4 | 253.53 | No | - | 600.29 | 7.04 | 0.92 | 6.79 | 1.63 | 25.38 | 215.7 | 0.46
2024-03-11 | 2024-05-21 | 0.0 | 0.0 | 0.0 | N-3 | 252.79 | No | - | 577.15 | 7.02 | 0.89 | 6.60 | 0.00 | 25.81 | 319.8 | 0.44
2024-03-11 | 2024-06-07 | 0.0 | 0.0 | 0.0 | N-5 | 252.87 | No | - | 582.18 | 6.98 | 0.90 | 6.84 | 0.92 | 26.23 | 280.4 | 0.45
2024-03-11 | 2024-06-21 | 0.0 | 0.0 | 0.0 | N-5 | 252.87 | No | - | 597.89 | 6.93 | 0.92 | 7.56 | 0.49 | 25.97 | 301.5 | 0.46
2024-03-11 | 2024-07-05 | 0.0 | 0.0 | 0.0 | N-4 | 252.9 | No | - | 580.87 | 7.03 | 0.89 | 6.88 | 0.00 | 25.47 | 274.5 | 0.44
2024-03-11 | 2024-07-19 | 0.0 | 0.0 | 0.0 | N-3 | 252.83 | No | - | 590.21 | 7.00 | 0.91 | 6.90 | 3.18 | 25.52 | 211.8 | 0.45
2024-03-11 | 2024-08-06 | 0.0 | 0.0 | 0.0 | N-3 | 253.02 | No | - | 652.21 | 6.96 | 1.00 | 7.23 | 0.29 | 26.09 | 282.8 | 0.50
2024-03-11 | 2024-08-19 | 0.0 | 0.0 | 0.0 | N-3 | 252.83 | No | - | 660.02 | 7.06 | 1.02 | 7.10 | 1.20 | 25.96 | 314.6 | 0.51
2024-03-11 | 2024-09-06 | 0.0 | 0.0 | 0.0 | N-4 | 252.72 | No | - | 609.99 | 6.98 | 0.94 | 7.17 | 0.50 | 25.90 | 238.2 | 0.47
2024-03-11 | 2024-09-20 | 0.0 | 0.0 | 0.0 | 288404 | 252.64 | No | - | 661.85 | 6.94 | 1.02 | 7.17 | 0.00 | 25.73 | 320.4 | 0.51
2024-03-11 | 2024-10-10 | 0.0 | 0.0 | 0.0 | N-4 | 252.73 | No | - | 620.44 | 7.20 | 0.95 | 7.13 | 0.65 | 26.05 | 209.0 | 0.48
2024-03-11 | 2024-10-22 | 0.0 | 0.0 | 0.0 | N-3 | 252.73 | No | - | 617.53 | 7.09 | 0.95 | 7.19 | 1.15 | 26.16 | 123.9 | 0.47
2024-03-11 | 2024-11-04 | 0.0 | 0.0 | 0.0 | N-4 | 252.68 | No | - | 668.22 | 7.11 | 1.03 | 7.09 | 0.00 | 25.54 | 152.1 | 0.51
2024-03-11 | 2024-11-19 | 0.0 | 0.0 | 0.0 | N-5 | 252.64 | No | - | 594.17 | 7.06 | 0.91 | 7.14 | 1.56 | 25.63 | 168.5 | 0.45
2024-03-11 | 2024-12-03 | 0.0 | 0.0 | 0.0 | N-4 | 252.54 | No | - | 625.24 | 6.92 | 0.96 | 6.98 | 0.00 | 25.75 | 203.3 | 0.48
2024-03-11 | 2024-12-17 | 0.0 | 0.0 | 0.0 | N-5 | 252.53 | No | - | 641.81 | 6.97 | 0.99 | 7.07 | 1.03 | 25.88 | 245.7 | 0.49
| RHP07 Headspace and Product Gauging | [7 empty] | RHP07 Parameter Readings
WEEK | DATE | AMBIENT | TOP-OF-CASING HEADSPACE | GROUNDWATER HEADSPACE | TAPE | DTW (Raw) | PRODUCT? | THICKNESS | TDS | pH | Sp. Cond. | D.O. | Turbidity | TEMP | ORP | SAL
|  | (ppmv) | (ppmv) | (ppmv) | (Serial #) | (ft btoc) | (Yes/No) | (ft) | (ppm) |  | (mS/cm) | (mg/L) | (NTU) | (°C) | (Mv) | (psu)
06/12/2023 | 06/15/2023 | 0.0 | 0.0 | - | N-4 | 82.37 | No | - | 403.36 | 7.40 | 0.62 | 8.08 | 0.12 | 23.57 | 152.5 | 0.30
07/03/2023 | 07/03/2023 | 0.0 | 0.0 | - | N-4 | 83.08 | No | - | 388.13 | 7.43 | 0.60 | 8.13 | 0.02 | 23.32 | 269.6 | 0.29
07/31/2023 | 08/02/2023 | 0.2 | 0.5 | - | N-3 | 83.22 | No | - | 379.68 | 7.42 | 0.58 | 7.96 | 0.06 | 23.45 | 114.6 | 0.29
09/04/2023 | 09/06/2023 | 0.0 | 0.0 | - | N-4 | 83.36 | No | - | 393.42 | 7.12 | 0.61 | 8.31 | 0.02 | 23.23 | 150.2 | 0.30
10/02/2023 | 10/05/2023 | 0.0 | 0.0 | - | N-4 | 83.56 | No | - | 386.21 | 7.31 | 0.59 | 7.91 | 0.00 | 23.21 | 271.0 | 0.29
10/16/2023 | 10/17/2023 | 0.0 | 0.0 | - | N-5 | 83.54 | No | - | 383.20 | 7.42 | 0.59 | 7.83 | 0.24 | 23.28 | 108.9 | 0.29
10/23/2023 | 10/24/2023 | 0.0 | 0.0 | - | N-3 | 83.55 | No | - | 373.04 | 7.37 | 0.57 | 8.34 | 0.16 | 23.40 | 228.5 | 0.28
10/30/2023 | 10/31/2023 | 0.0 | 0.1 | - | N-4 | 83.54 | No | - | 383.03 | 7.41 | 0.59 | 7.90 | 0.00 | 23.33 | 295.1 | 0.29
11/06/2023 | 11/10/2023 | 0.0 | 0.0 | - | N-3 | 83.59 | No | - | 383.65 | 7.41 | 0.60 | 8.00 | 0.13 | 23.45 | 276.1 | 0.29
2023-11-13 | 2023-11-14 | 0.0 | 0.0 | - | N-5 | 83.86 | No | - | 388.05 | 7.34 | 0.60 | 8.14 | 0.99 | 23.34 | 299.6 | 0.29
2023-11-20 | 2023-11-21 | 0.0 | 0.0 | - | N-4 | 83.67 | No | - | 364.24 | 7.39 | 0.56 | 7.98 | 0.39 | 23.18 | 213.4 | 0.27
2023-11-27 | 2023-11-28 | 0.0 | 0.0 | - | N-4 | 83.53 | No | - | 373.37 | 7.38 | 0.57 | 7.87 | 0.11 | 23.33 | 269.4 | 0.28
2023-12-04 | 2023-12-05 | 0.0 | 0.0 | - | N-5 | 83.43 | No | - | 367.09 | 7.31 | 0.56 | 8.15 | 0.06 | 23.46 | 269.4 | 0.28
2023-12-11 | 2023-12-12 | 0.0 | 0.0 | - | N-3 | 83.4 | No | - | 354.71 | 7.32 | 0.55 | 8.15 | 0.04 | 23.37 | 278.6 | 0.27
2023-12-18 | 2023-12-22 | 0.0 | 0.0 | - | N-4 | 83.33 | No | - | 362.13 | 7.33 | 0.56 | 8.13 | 0.00 | 23.19 | 252.3 | 0.27
2023-12-25 | 2023-12-29 | 0.0 | 0.2 | - | N-4 | 83.33 | No | - | 391.03 | 7.33 | 0.60 | 8.25 | 0.07 | 23.36 | 267.9 | 0.29
2024-01-01 | 2024-01-02 | 0.0 | 0.0 | - | N-5 | 83.33 | No | - | 363.10 | 7.31 | 0.56 | 8.29 | 0.00 | 23.13 | 312.2 | 0.27
2024-01-08 | 2024-01-09 | 0.0 | 0.7 | - | N-5 | 83.22 | No | - | 379.95 | 7.24 | 0.58 | 8.19 | 0.58 | 23.38 | 320.1 | 0.29
2024-01-15 | 2024-01-16 | 0.0 | 0.1 | - | N-6 | 83.12 | No | - | 379.95 | 7.26 | 0.58 | 7.87 | 0.49 | 23.44 | 319.2 | 0.28
2024-02-05 | 2024-02-06 | 0.3 | 0.2 | - | N-5 | 83.17 | No | - | 373.65 | 7.18 | 0.57 | 8.04 | 0.70 | 23.24 | 213.4 | 0.28
2024-03-11 | 2024-03-12 | 0.0 | 0.0 | - | N-5 | 83.14 | No | - | 369.44 | 7.22 | 0.57 | 8.18 | 1.16 | 23.12 | 252.6 | 0.28
2024-03-11 | 2024-04-02 | 0.0 | 0.0 | - | N-5 | 83.21 | No | - | 387.50 | 7.24 | 0.60 | 7.76 | 0.43 | 23.10 | 236.7 | 0.29
2024-03-11 | 2024-05-08 | 0.0 | 0.1 | 0.0 | N-5 | 82.95 | No | - | 375.26 | 7.26 | 0.58 | 8.01 | 0.75 | 23.34 | 232.3 | 0.28
2024-03-11 | 2024-05-22 | 0.0 | 0.0 | 0.0 | N-3 | 82.18 | No | - | 413.68 | 7.31 | 0.64 | 8.26 | 1.16 | 23.27 | 324.7 | 0.31
2024-03-11 | 2024-06-05 | 0.0 | 0.0 | 0.0 | N-4 | 82.66 | No | - | 386.57 | 7.16 | 0.59 | 8.17 | 3.10 | 23.26 | 257.2 | 0.29
2024-03-11 | 2024-06-18 | 0.2 | 0.0 | 0.0 | N-4 | 82.06 | No | - | 384.94 | 7.42 | 0.59 | 8.16 | 0.00 | 23.27 | 211.7 | 0.29
2024-03-11 | 2024-07-03 | 0.0 | 0.0 | 0.0 | N-4 | 82.8 | No | - | 396.27 | 7.31 | 0.61 | 8.31 | 0.00 | 23.26 | 291.4 | 0.30
2024-03-11 | 2024-07-17 | 0.0 | 0.0 | 0.0 | N-3 | 82.38 | No | - | 408.15 | 7.31 | 0.63 | 8.26 | 2.56 | 23.32 | 246.3 | 0.31
2024-03-11 | 2024-08-07 | 0.0 | 0.0 | 0.0 | N-5 | 82.38 | No | - | 411.69 | 7.27 | 0.63 | 8.21 | 0.00 | 23.36 | 272.7 | 0.31
2024-03-11 | 2024-08-21 | 0.0 | 0.0 | 0.0 | N-5 | 82.57 | No | - | 420.45 | 7.38 | 0.65 | 8.59 | 0.00 | 23.35 | 333.0 | 0.32
2024-03-11 | 2024-09-05 | 0.0 | 0.0 | 0.0 | N-5 | 82.55 | No | - | 386.72 | 7.44 | 0.59 | 8.35 | 0.07 | 23.41 | 236.5 | 0.29
2024-03-11 | 2024-09-18 | 0.0 | 0.0 | 0.0 | 252094 | 82.64 | No | - | 433.64 | 7.39 | 0.67 | 8.50 | 4.45 | 23.23 | 297.6 | 0.33
2024-03-11 | 2024-10-23 | 0.0 | 0.0 | 0.0 | N-4 | 82.48 | No | - | 430.63 | 7.34 | 0.66 | 8.24 | 6.14 | 23.28 | 169.9 | 0.33
2024-03-11 | 2024-11-06 | 0.0 | 0.0 | 0.0 | N-4 | 82.43 | No | - | 393.16 | 7.47 | 0.60 | 8.34 | 0.79 | 23.41 | 87.0 | 0.30
2024-03-11 | 2024-11-20 | 0.0 | 0.0 | 0.0 | N-5 | 82.34 | No | - | 418.17 | 7.35 | 0.64 | 8.24 | 0.88 | 23.29 | 163.3 | 0.32
2024-03-11 | 2024-12-04 | 0.0 | 0.0 | 0.0 | N-3 | 82.08 | No | - | 401.13 | 7.33 | 0.62 | 8.43 | 1.86 | 23.09 | 223.0 | 0.30
2024-03-11 | 2024-12-18 | 0.0 | 0.0 | 0.0 | N-3 | 82.1 | No | - | 406.69 | 7.26 | 0.63 | 8.34 | 0.18 | 23.16 | 239.3 | 0.31
| RHP08 Headspace and Product Gauging | [7 empty] | RHP08 Parameter Readings
WEEK | DATE | AMBIENT | TOP-OF-CASING HEADSPACE | GROUNDWATER HEADSPACE | TAPE | DTW (Raw) | PRODUCT? | THICKNESS | TDS | pH | Sp. Cond. | D.O. | Turbidity | TEMP | ORP | SAL
|  | (ppmv) | (ppmv) | (ppmv) | (Serial #) | (ft btoc) | (Yes/No) | (ft) | (ppm) |  | (mS/cm) | (mg/L) | (NTU) | (°C) | (Mv) | (psu)
09/11/2023 | 09/11/2023 | 0.0 | 0.4 | - | N-4 | 285.7 | No | - | 415.92 | 8.08 | 0.64 | 2.68 | 0.84 | 26.86 | -50.3 | 0.31
10/02/2023 | 10/03/2023 | 0.1 | 0.5 | - | N-4 | 285.76 | No | - | 417.86 | 7.77 | 0.64 | 4.30 | 0.65 | 26.35 | 150.3 | 0.32
10/23/2023 | 10/27/2023 | 0.0 | 0.5 | - | N-4 | 285.79 | No | - | 442.26 | 7.75 | 0.68 | 5.10 | 0.82 | 25.56 | 248.0 | 0.33
10/30/2023 | 11/02/2023 | 0.0 | 0.0 | - | N-3 | 285.82 | No | - | 416.43 | 7.76 | 0.64 | 5.33 | 0.65 | 26.21 | 216.7 | 0.31
11/06/2023 | 11/06/2023 | 0.0 | 0.5 | - | N-4 | 285.82 | No | - | 425.34 | 7.72 | 0.70 | 5.30 | 0.00 | 25.79 | 227.1 | 0.32
2023-11-13 | 2023-11-13 | 0.0 | 0.0 | - | N-3 | 285.86 | No | - | 418.99 | 7.74 | 0.64 | 5.79 | 0.00 | 25.43 | 224.7 | 0.32
2023-11-20 | 2023-11-21 | 0.0 | 0.0 | - | N-6 | 285.86 | No | - | 421.66 | 7.65 | 0.65 | 5.50 | 0.98 | 25.01 | 151.7 | 0.32
2023-11-27 | 2023-11-29 | 0.3 | 0.3 | - | N-6 | 285.73 | No | - | 403.16 | 7.68 | 0.62 | 5.90 | 0.63 | 24.72 | 205.5 | 0.30
2023-12-04 | 2023-12-05 | 0.0 | 0.0 | - | N-3 | 285.72 | No | - | 412.91 | 7.69 | 0.64 | 5.65 | 5.37 | 24.91 | 203.6 | 0.31
2023-12-11 | 2023-12-13 | 0.0 | 0.0 | - | N-6 | 285.7 | No | - | 408.61 | 7.72 | 0.63 | 5.69 | 0.58 | 25.14 | 212.7 | 0.31
2023-12-18 | 2023-12-20 | 0.0 | 0.0 | - | N-6 | 285.67 | No | - | 402.98 | 7.66 | 0.62 | 6.04 | 0.73 | 24.49 | 172.2 | 0.30
2023-12-25 | 2023-12-28 | 0.0 | 0.0 | - | N-6 | 285.64 | No | - | 399.11 | 7.71 | 0.61 | 5.94 | 1.08 | 24.83 | 190.8 | 0.30
2024-01-01 | 2024-01-02 | 0.0 | 0.0 | - | N-4 | 285.69 | No | - | 397.29 | 7.72 | 0.61 | 6.18 | 1.38 | 24.74 | 229.9 | 0.30
2024-01-08 | 2024-01-10 | 0.0 | 0.0 | - | N-6 | 285.52 | No | - | 415.54 | 7.69 | 0.64 | 5.91 | 1.09 | 24.90 | 229.2 | 0.31
2024-01-15 | 2024-01-15 | 0.0 | 0.3 | - | N-3 | 285.48 | No | - | 420.31 | 7.73 | 0.65 | 6.03 | 0.68 | 24.45 | 211.3 | 0.32
2024-02-05 | 2024-02-07 | 0.0 | 7.5 | - | N-5 | 285.51 | No | - | 381.41 | 7.67 | 0.59 | 6.07 | 1.68 | 24.72 | 176.9 | 0.29
2024-03-18 | 2024-03-18 | 0.0 | 0.0 | - | N-6 | 285.53 | No | - | 384.47 | 7.71 | 0.59 | 6.68 | 1.72 | 25.12 | 251.0 | 0.29
2024-03-18 | 2024-04-05 | 0.0 | 0.0 | - | N-6 | 285.6 | No | - | 447.48 | 7.72 | 0.69 | 6.65 | 8.52 | 25.24 | 263.9 | 0.34
2024-03-18 | 2024-05-10 | 0.0 | 0.0 | 0.0 | N-4 | 285.26 | No | - | 466.02 | 7.51 | 0.72 | 6.93 | 2.99 | 25.70 | 202.5 | 0.35
2024-03-18 | 2024-05-21 | 0.0 | 0.0 | 0.0 | N-3 | 284.96 | No | - | 497.08 | 7.52 | 0.76 | 7.32 | 2.86 | 25.08 | 296.9 | 0.38
2024-03-18 | 2024-06-07 | 0.0 | 0.0 | 0.0 | N-5 | 284.99 | No | - | 458.93 | 7.48 | 0.71 | 7.19 | 1.79 | 25.31 | 243.4 | 0.35
2024-03-18 | 2024-06-21 | 0.0 | 0.0 | 0.0 | N-5 | 285.02 | No | - | 453.56 | 7.48 | 0.70 | 7.99 | 0.33 | 25.13 | 279.8 | 0.34
2024-03-18 | 2024-07-05 | 0.0 | 0.4 | 0.0 | N-4 | 285.13 | No | - | 417.36 | 8.11 | 0.64 | 6.72 | 0.31 | 25.60 | 220.5 | 0.32
2024-03-18 | 2024-07-18 | 0.0 | 0.0 | 0.0 | N-3 | 285.08 | No | - | 427.52 | 7.57 | 0.66 | 7.24 | 0.58 | 25.69 | 208.0 | 0.32
2024-03-18 | 2024-08-06 | 0.0 | 0.0 | 0.0 | N-3 | 285.2 | No | - | 415.43 | 7.69 | 0.64 | 6.78 | 2.80 | 26.10 | 257.6 | 0.31
2024-03-18 | 2024-08-19 | 0.0 | 0.0 | 0.0 | N-3 | 285.05 | No | - | 459.52 | 7.63 | 0.71 | 6.94 | 0.23 | 25.69 | 317.8 | 0.35
2024-03-18 | 2024-09-09 | 0.0 | 0.0 | 0.0 | N-5 | 284.77 | No | - | 432.00 | 7.58 | 0.66 | 7.57 | 4.62 | 25.40 | 199.0 | 0.33
2024-03-18 | 2024-09-17 | 0.0 | 0.0 | 0.0 | 288404 | 285.03 | No | - | 422.58 | 7.78 | 0.65 | 6.80 | 2.57 | 25.54 | 264.2 | 0.32
2024-03-18 | 2024-10-03 | 0.0 | 0.0 | 0.0 | N-4 | 284.78 | No | - | 487.89 | 7.56 | 0.75 | 7.49 | 0.09 | 25.31 | 226.2 | 0.37
2024-03-18 | 2024-10-22 | 0.0 | 0.0 | 0.0 | N-3 | 284.95 | No | - | 410.42 | 7.71 | 0.63 | 7.11 | 3.33 | 25.04 | 132.2 | 0.31
2024-03-18 | 2024-11-04 | 0.0 | 0.0 | 0.0 | N-4 | 284.78 | No | - | 481.48 | 7.47 | 0.74 | 7.50 | 10.63 | 25.00 | 113.6 | 0.37
2024-03-18 | 2024-11-19 | 0.0 | 0.0 | 0.0 | N-5 | 284.84 | No | - | 403.72 | 7.69 | 0.62 | 7.20 | 4.94 | 25.01 | 140.2 | 0.30
2024-03-18 | 2024-12-03 | 0.0 | 0.0 | 0.0 | N-4 | 284.73 | No | - | 483.58 | 7.45 | 0.74 | 7.41 | 17.25 | 24.83 | 176.5 | 0.37
2024-03-18 | 2024-12-17 | 0.0 | 0.0 | 0.0 | N-5 | 284.69 | No | - | 502.77 | 7.46 | 0.77 | 7.53 | 0.58 | 25.04 | 240.3 | 0.38
| RHP08B Headspace and Product Gauging | [7 empty] | RHP08B Parameter Readings
WEEK | DATE | AMBIENT | TOP-OF-CASING HEADSPACE | GROUNDWATER HEADSPACE | TAPE | DTW (Raw) | PRODUCT? | THICKNESS | TDS | pH | Sp. Cond. | D.O. | Turbidity | TEMP | ORP | SAL
|  | (ppmv) | (ppmv) | (ppmv) | (Serial #) | (ft btoc) | (Yes/No) | (ft) | (ppm) |  | (mS/cm) | (mg/L) | (NTU) | (°C) | (Mv) | (psu)
09/11/2023 | 2024-09-27 | 0.0 | 0.0 | - | N-4 | 290.92 | No | - | 394.22 | 7.95 | 0.61 | 16.00 | 7.75 | 30.43 | 217.2 | 0.30
09/11/2023 | 2024-10-16 | 0.0 | 0.0 | - | N-3 | 290.98 | No | - | 403.33 | 8.02 | 0.62 | 15.54 | 1.13 | 26.87 | 201.3 | 0.30
09/11/2023 | 2024-10-30 | 0.0 | 0.0 | - | N-4 | 291 | No | - | 349.62 | 8.09 | 0.54 | 13.11 | 12.98 | 26.29 | 69.5 | 0.26
09/11/2023 | 2024-11-14 | 0.0 | 0.0 | - | N-4 | 290.93 | No | - | 404.11 | 8.04 | 0.62 | 13.40 | 0.27 | 25.86 | 138.5 | 0.30
09/11/2023 | 2024-11-24 | 0.0 | 0.0 | - | N-5 | 290.62 | No | - | 358.26 | 8.35 | 0.55 | 14.13 | 1.14 | 25.72 | 194.8 | 0.27
09/11/2023 | 2024-12-12 | 0.0 | 0.0 | - | N-3 | 290.82 | No | - | 375.24 | 8.42 | 0.58 | 13.32 | 0.82 | 25.98 | 147.3 | 0.28
09/11/2023 | 2024-12-27 | 0.0 | 0.0 | - | N-3 | 290.83 | No | - | 359.59 | 8.56 | 0.55 | 15.02 | 0.67 | 25.47 | 243.2 | 0.27
| RHP08C Headspace and Product Gauging | [7 empty] | RHP08C Parameter Readings
WEEK | DATE | AMBIENT | TOP-OF-CASING HEADSPACE | GROUNDWATER HEADSPACE | TAPE | DTW (Raw) | PRODUCT? | THICKNESS | TDS | pH | Sp. Cond. | D.O. | Turbidity | TEMP | ORP | SAL
|  | (ppmv) | (ppmv) | (ppmv) | (Serial #) | (ft btoc) | (Yes/No) | (ft) | (ppm) |  | (mS/cm) | (mg/L) | (NTU) | (°C) | (Mv) | (psu)
09/11/2023 | 2024-08-14 | 0.0 | 0.0 | - | N-3 | 290.88 | No | - | 338.76 | 8.58 | 0.52 | 8.49 | 0.93 | 27.80 | 155.8 | 0.25
09/11/2023 | 2024-08-27 | 0.0 | 0.0 | - | N-4 | 291.12 | No | - | 358.36 | 8.36 | 0.55 | 8.16 | 0.12 | 26.79 | 277.5 | 0.27
09/11/2023 | 2024-09-13 | 0.0 | 0.0 | - | 288404 | 290.87 | No | - | 359.18 | 8.59 | 0.55 | 7.76 | 0.68 | 27.01 | 225.8 | 0.27
09/11/2023 | 2024-09-27 | 0.0 | 0.0 | - | N-4 | 290.9 | No | - | 331.61 | 8.60 | 0.51 | 7.95 | 0.38 | 26.42 | 196.0 | 0.25
09/11/2023 | 2024-10-16 | 0.0 | 0.0 | - | N-5 | 290.97 | No | - | 327.70 | 8.34 | 0.50 | 8.03 | 0.91 | 26.05 | 226.0 | 0.25
09/11/2023 | 2024-10-30 | 0.0 | 0.0 | - | N-3 | 290.94 | No | - | 364.50 | 8.22 | 0.56 | 8.17 | 1.90 | 26.10 | 81.0 | 0.27
09/11/2023 | 2024-11-14 | 0.0 | 0.0 | - | N-4 | 290.87 | No | - | 365.90 | 8.26 | 0.56 | 7.86 | 1.31 | 25.61 | 128.1 | 0.28
09/11/2023 | 2024-11-24 | 0.0 | 0.0 | - | N-5 | 290.66 | No | - | 341.85 | 8.50 | 0.53 | 7.31 | 3.20 | 25.35 | 177.9 | 0.26
09/11/2023 | 2024-12-12 | 0.0 | 0.0 | - | N-3 | 290.8 | No | - | 343.77 | 8.33 | 0.53 | 7.72 | 0.77 | 25.56 | 135.8 | 0.26
09/11/2023 | 2024-12-27 | 0.0 | 0.0 | - | N-4 | 290.87 | No | - | 330.73 | 8.39 | 0.51 | 7.54 | 1.71 | 25.63 | 175.5 | 0.25

## Legend
Red Hill Bulk Fuel Storage Facility Notice of Interest 20210507-0852 (6 May 2021 Event) Notice of Interest 20211120-2330 (20 Nov 2021 Event) Headspace, Fuel Product Gauging, and Parameters
Notes:
NC = Not collected
NM = No measurement taken, due to equipment installed in well.
DTW = Depth-to-water
ft = feet
ft btoc = feet below top of casing
- = Not applicable / no data available
ppmv = parts-per-million by volume
Depth to water measurements correction factors for Solinst groundwater-level measuring tapes N-1 through N-6 using the USGS calibration results are published in letters titled “Results from Calibration of Groundwater-Level Measuring Tapes” dated January 24, 2020 (N-1 and N-2) and December 14, 2022 (N 1, N-2, N-3, N-4, N 5 and N-6). Depth to water measurements correction factors for horizontal well displacement are derived from gyroscopic survey results for wells RHMW01R through RHMW19, OWDFMW01 through OWDFMW08A, HDMW2253-03, NMW24, RHP01 through RHP04A, RHP04C, and RHP07 and are pending results for recently installed wells. Groundwater-level measuring tape and horizontal displacement correction factors for N-1 through N-6 for all wells are shown on “Correction Factor Tables”.
Headspace is measured from top-of-casing for all monitoring wells. Additionally, starting in May 2024 with the implementation of the Consolidation and Optimization of the Groundwater Sampling Programs, Red Hill Bulk Fuel Storage Facility sampling plan, groundwater headspace VOCs are measured from: 1. All monitoring wells installed in unconfined conditions (i.e., with unsubmerged screens) from surface water collected via bailer prior to sampling. 2. All Westbay monitoring wells collected directly from the sample canister.
All Westbay Wells - Westbay is a closed system and the sample port is not located at the water's surface, therefore free product will not be captured or observed. Headspace is measured from Westbay wells for almost all canister pulls. The highest reading measured for each sample is shown in this spreadsheet. Samples collected from Westbay wells are observed for free product during collection and will be noted.
RHP01 - 06/16/2023: Well added as part of the consolidated groundwater sampling program
RHP02 - 06/16/2023: Well added as part of the consolidated groundwater sampling program
RHP03 - 06/16/2023: Well added as part of the consolidated groundwater sampling program
RHP04A - 06/14/2023: Well added as part of the consolidated groundwater sampling program
RHP04B - 06/14/2023: Well added as part of the consolidated groundwater sampling program
RHP04C - 06/16/2023: Well added as part of the consolidated groundwater sampling program
RHP05 - 06/16/2023: Well added as part of the consolidated groundwater sampling program
RHP06 - 07/24/2023: Well added as part of the consolidated groundwater sampling program
RHP07 - 06/15/2023: Well added as part of the consolidated groundwater sampling program
RHP08 - 09/11/2023: Well added as part of the consolidated groundwater sampling program
RHP08B - 09/27/2024: Well added as part of the consolidated groundwater sampling program
RHP08C - 08/14/2024: Well added as part of the consolidated groundwater sampling program
NMW24 - 06/07/2023: Well added as part of the consolidated groundwater sampling program
NMW25 - 07/26/2023: Well added as part of the consolidated groundwater sampling program
NMW26 - 02/02/2024: Well added as part of the consolidated groundwater sampling program
NMW27 - 10/09/2024: Well added as part of the consolidated groundwater sampling program. Note initial depth-to-water measurement is from top of casing prior to well completion.
NMW30 - 10/19/2023: Well added as part of the consolidated groundwater sampling program
NMW32 - 08/29/2023: Well added as part of the consolidated groundwater sampling program
NMW33 - 10/03/2023: Well added as part of the consolidated groundwater sampling program
NMW34 - 03/19/2024: Well added as part of the consolidated groundwater sampling program
OWDFMW03A - 05/15/2024: Well added as part of the consolidated groundwater sampling program
OWDFMW08A - 05/15/2024: Well added as part of the consolidated groundwater sampling program
RHMW03 - 09/07/2023: AquaTroll turbidity sensor wiper not turned on or missing causing bubbles to accumulate on the turbidity sensor and affecting parameter accuracy.
RHMW10 - 06/12/2023: Well added as part of the consolidated groundwater sampling program
RHMW10 - 12/13/2023: AquaTroll specific conductivity/TDS/salinity sensor malfunction resulting in loss of recordable data. Parameter stabilization criteria met prior to sampling.
RHMW13 Zone 5 - 09/05/2023: Temperature reading higher than expected due to issue with temperature sensor.
RHMW12A - All readings: Well screen is submerged and does not span the water's surface, therefore free product will not be captured or observed. Wells with submerged screens have a one-time bailer sample collected to verfiy no free product at the waters surface.
RHMW16 - All readings: Well screen is submerged and does not span the water's surface, therefore free product will not be captured or observed. Wells with submerged screens have a one-time bailer sample collected to verfiy no free product at the waters surface.
RHMW18 - 12/31/2023: Well added as part of the consolidated groundwater sampling program
RHMW19 - 12/19/2023: AquaTroll RDO sensor malfunction resulting in loss of recordable data. Parameter stabilization criteria met prior to sampling.
RHMW20 - 06/14/2023: Well added as part of the consolidated groundwater sampling program
RHMW21 - 07/22/2024: Well added as part of the consolidated groundwater sampling program

## Tape Correction Factors
Red Hill Bulk Fuel Storage Facility Notice of Interest 20210507-0852 (6 May 2021 Event) Notice of Interest 20211120-2330 (20 Nov 2021 Event) Headspace, Fuel Product Gauging, and Parameters
Tape Correction
Serial Number | Calibration Date | Beginning Depth (ft) | End Depth (ft) | Correction (ft)
N-1 | 2017 | 0.00 | 6.41 | 0.00
N-1 | 2017 | 6.42 | 14.02 | 0.00
N-1 | 2017 | 14.03 | 52.17 | -0.01
N-1 | 2017 | 52.18 | 90.33 | -0.02
N-1 | 2017 | 90.34 | 128.49 | -0.03
N-1 | 2017 | 128.50 | 166.64 | -0.04
N-1 | 2017 | 166.65 | 204.80 | -0.05
N-1 | 2017 | 204.81 | 242.96 | -0.06
N-1 | 2017 | 242.97 | 392.45 | -0.07
N-1 | 2017 | 392.46 | 500.00 | -0.07
N-2 | 2017 | 0.00 | 6.40 | 0.01
N-2 | 2017 | 6.41 | 8.23 | 0.01
N-2 | 2017 | 8.24 | 80.71 | 0.00
N-2 | 2017 | 80.72 | 161.31 | -0.01
N-2 | 2017 | 161.32 | 253.61 | -0.02
N-2 | 2017 | 253.62 | 364.91 | -0.03
N-2 | 2017 | 364.92 | 516.53 | -0.04
N-2 | 2017 | 516.54 | 593.17 | -0.05
N-2 | 2017 | 593.18 | 764.02 | -0.05
N-2 | 2017 | 764.03 | 1000.00 | -0.06
N-1 | 2019 | 0.00 | 6.30 | 0.00
N-1 | 2019 | 6.31 | 29.17 | 0.00
N-1 | 2019 | 29.18 | 108.72 | -0.01
N-1 | 2019 | 108.73 | 188.27 | -0.02
N-1 | 2019 | 188.28 | 267.83 | -0.03
N-1 | 2019 | 267.84 | 347.38 | -0.04
N-1 | 2019 | 347.39 | 392.07 | -0.05
N-1 | 2019 | 392.08 | 426.93 | -0.05
N-1 | 2019 | 426.94 | 500.00 | -0.06
N-2 | 2019 | 0.00 | 6.29 | 0.00
N-2 | 2019 | 6.30 | 48.47 | 0.00
N-2 | 2019 | 48.48 | 113.38 | -0.01
N-2 | 2019 | 113.39 | 181.28 | -0.02
N-2 | 2019 | 181.29 | 252.63 | -0.03
N-2 | 2019 | 252.64 | 328.02 | -0.04
N-2 | 2019 | 328.03 | 408.23 | -0.05
N-2 | 2019 | 408.24 | 494.31 | -0.06
N-2 | 2019 | 494.32 | 587.79 | -0.07
N-2 | 2019 | 587.80 | 592.86 | -0.08
N-2 | 2019 | 592.87 | 690.98 | -0.08
N-2 | 2019 | 690.99 | 807.72 | -0.09
N-2 | 2019 | 807.73 | 945.40 | -0.10
N-2 | 2019 | 945.41 | 1000.00 | -0.11
N-1 | 2022 | 0.00 | 18.17 | 0.01
N-1 | 2022 | 18.18 | 24.44 | 0.01
N-1 | 2022 | 24.45 | 49.50 | 0.00
N-1 | 2022 | 49.51 | 74.57 | -0.01
N-1 | 2022 | 74.58 | 99.64 | -0.02
N-1 | 2022 | 99.65 | 124.71 | -0.03
N-1 | 2022 | 124.72 | 149.78 | -0.04
N-1 | 2022 | 149.79 | 174.84 | -0.05
N-1 | 2022 | 174.85 | 199.91 | -0.06
N-1 | 2022 | 199.92 | 224.98 | -0.07
N-1 | 2022 | 224.99 | 250.05 | -0.08
N-1 | 2022 | 250.06 | 275.11 | -0.09
N-1 | 2022 | 275.12 | 393.17 | -0.10
N-1 | 2022 | 393.18 | 500.00 | -0.10
N-2 | 2022 | 0.00 | 7.39 | -0.01
N-2 | 2022 | 7.40 | 18.18 | -0.02
N-2 | 2022 | 18.19 | 28.82 | -0.02
N-2 | 2022 | 28.83 | 51.17 | -0.03
N-2 | 2022 | 51.18 | 74.58 | -0.04
N-2 | 2022 | 74.59 | 99.21 | -0.05
N-2 | 2022 | 99.22 | 125.27 | -0.06
N-2 | 2022 | 125.28 | 153.06 | -0.07
N-2 | 2022 | 153.07 | 182.96 | -0.08
N-2 | 2022 | 182.97 | 215.55 | -0.09
N-2 | 2022 | 215.56 | 251.71 | -0.10
N-2 | 2022 | 251.72 | 292.97 | -0.11
N-2 | 2022 | 292.98 | 342.39 | -0.12
N-2 | 2022 | 342.40 | 408.44 | -0.13
N-2 | 2022 | 408.45 | 685.51 | -0.14
N-2 | 2022 | 685.52 | 751.56 | -0.13
N-2 | 2022 | 751.57 | 800.98 | -0.12
N-2 | 2022 | 800.99 | 831.56 | -0.11
N-2 | 2022 | 831.57 | 842.44 | -0.11
N-2 | 2022 | 842.45 | 882.26 | -0.10
N-2 | 2022 | 882.27 | 922.08 | -0.09
N-2 | 2022 | 922.09 | 961.90 | -0.08
N-2 | 2022 | 961.91 | 1000.00 | -0.07
N-3 | 2022 | 0.00 | 7.03 | 0.00
N-3 | 2022 | 7.04 | 18.18 | -0.01
N-3 | 2022 | 18.19 | 20.83 | -0.01
N-3 | 2022 | 20.84 | 35.47 | -0.02
N-3 | 2022 | 35.48 | 51.15 | -0.03
N-3 | 2022 | 51.16 | 68.11 | -0.04
N-3 | 2022 | 68.12 | 86.74 | -0.05
N-3 | 2022 | 86.75 | 107.64 | -0.06
N-3 | 2022 | 107.65 | 131.96 | -0.07
N-3 | 2022 | 131.97 | 162.22 | -0.08
N-3 | 2022 | 162.23 | 208.21 | -0.09
N-3 | 2022 | 208.22 | 308.99 | -0.10
N-3 | 2022 | 309.00 | 354.98 | -0.09
N-3 | 2022 | 354.99 | 385.24 | -0.08
N-3 | 2022 | 385.25 | 393.15 | -0.07
N-3 | 2022 | 393.16 | 410.56 | -0.07
N-3 | 2022 | 410.57 | 435.64 | -0.06
N-3 | 2022 | 435.65 | 460.72 | -0.05
N-3 | 2022 | 460.73 | 485.80 | -0.04
N-3 | 2022 | 485.81 | 500.00 | -0.03
N-4 | 2022 | 0.00 | 0.48 | -0.01
N-4 | 2022 | 0.49 | 11.83 | -0.02
N-4 | 2022 | 11.84 | 18.19 | -0.03
N-4 | 2022 | 18.20 | 23.66 | -0.03
N-4 | 2022 | 23.67 | 36.04 | -0.04
N-4 | 2022 | 36.05 | 49.06 | -0.05
N-4 | 2022 | 49.07 | 62.83 | -0.06
N-4 | 2022 | 62.84 | 77.49 | -0.07
N-4 | 2022 | 77.50 | 93.25 | -0.08
N-4 | 2022 | 93.26 | 110.39 | -0.09
N-4 | 2022 | 110.40 | 129.36 | -0.10
N-4 | 2022 | 129.37 | 150.90 | -0.11
N-4 | 2022 | 150.91 | 176.49 | -0.12
N-4 | 2022 | 176.50 | 209.96 | -0.13
N-4 | 2022 | 209.97 | 368.42 | -0.14
N-4 | 2022 | 368.43 | 393.21 | -0.13
N-4 | 2022 | 393.22 | 402.24 | -0.13
N-4 | 2022 | 402.25 | 433.12 | -0.12
N-4 | 2022 | 433.13 | 463.99 | -0.11
N-4 | 2022 | 464.00 | 494.86 | -0.10
N-4 | 2022 | 494.87 | 500.00 | -0.09
N-5 | 2022 | 0.00 | 3.66 | 0.03
N-5 | 2022 | 3.67 | 18.14 | 0.02
N-5 | 2022 | 18.15 | 32.69 | 0.02
N-5 | 2022 | 32.70 | 64.83 | 0.01
N-5 | 2022 | 64.84 | 101.37 | 0.00
N-5 | 2022 | 101.38 | 144.83 | -0.01
N-5 | 2022 | 144.84 | 201.87 | -0.02
N-5 | 2022 | 201.88 | 393.11 | -0.03
N-5 | 2022 | 393.12 | 500.00 | -0.03
N-6 | 2022 | 0.00 | 6.02 | -0.03
N-6 | 2022 | 6.03 | 18.20 | -0.04
N-6 | 2022 | 18.21 | 37.84 | -0.04
N-6 | 2022 | 37.85 | 72.83 | -0.05
N-6 | 2022 | 72.84 | 112.18 | -0.06
N-6 | 2022 | 112.19 | 158.10 | -0.07
N-6 | 2022 | 158.11 | 215.65 | -0.08
N-6 | 2022 | 215.66 | 305.93 | -0.09
N-6 | 2022 | 305.94 | 393.17 | -0.10
N-6 | 2022 | 393.18 | 750.00 | -0.10
Tape calibration conducted by USGS on: September 13 - 15, 2017; September 11 - 13, 2019; and September 20 - 22, 2022
Tape Correction for Week of September 19, 2022
Well | Rental Oil/Water Interface Probe SN | Rental Oil/Water Interface Probe DTW (ft) | Reference Oil/Water Interface Probe SN | Reference Oil/Water Interface Probe DTW (ft) | Oil/Water Interface Probe Offset (ft)
RHMW01R | 01-8854 | 83.80 | N-3 | 83.78 | -0.02
RHMW02 | 01-8854 | 86.70 | N-3 | 86.69 | -0.01
RHMW03 | 01-8854 | 102.93 | N-3 | 102.90 | -0.03
RHMW04 | 01-8854 | 294.30 | N-5 | 294.10 | -0.20
RHMW05 | 01-8854 | 83.40 | N-3 | 83.40 | 0.00
RHMW06 | 01-8854 | 241.25 | N-5 | 241.09 | -0.16
RHMW08 | 01-8854 | 292.81 | N-5 | 292.61 | -0.20
RHMW09 | 01-8607 | 378.09 | N-3 | 377.77 | -0.32
RHMW12A | 01-8854 | 220.85 | N-4 | 220.81 | -0.04
RHMW16 | 01-8854 | 202.07 | N-4 | 202.01 | -0.06
RHMW17 | 01-8854 | 234.51 | N-3 | 234.41 | -0.10
RHMW19 | 01-8607 | 427.27 | N-3 | 426.90 | -0.37
RHMW2254-01 | 01-8859 | 88.45 | N-3 | 88.51 | 0.06
OWDFMW01 | 287303 | 120.49 | N-3 | 120.38 | -0.11
OWDFMW04A | 25142 | 149.17 | N-4 | 149.16 | -0.01
OWDFMW05A | 25142 | 100.98 | N-4 | 100.98 | 0.00
OWDFMW07A | 25142 | 101.77 | N-4 | 101.77 | 0.00
OWDFMW08A | 25142 | 115.93 | N-4 | 115.93 | 0.00

## Horizontal Displacement Factors
Red Hill Bulk Fuel Storage Facility Notice of Interest 20210507-0852 (6 May 2021 Event) Notice of Interest 20211120-2330 (20 Nov 2021 Event) Headspace, Fuel Product Gauging, and Parameters
Monitoring Well Horizontal Displacement
Well | Horizontal Displacement Correction (ft)
RHMW01 | None
RHMW01R | -0.06
RHMW02 | -0.06
RHMW03 | -0.04
RHMW04 | -0.02
RHMW05 | -0.01
RHMW06 | -0.01
RHMW07 | -0.01
RHMW08 | -0.03
RHMW09 | -0.24
RHMW10 | -0.09
RHMW12A | -0.06
RHMW16 | -0.90
RHMW17 | -0.01
RHMW18 | pending
RHMW19 | -0.21
RHMW20 | pending
RHMW21 | pending
RHMW2254-01 | NA
OWDFMW01 | -0.03
OWDFMW03A | -0.07
OWDFMW04A | -0.03
OWDFMW05A | -0.03
OWDFMW07A | -0.08
OWDFMW08A | -0.08
HDMW2253-03 | -0.01
NMW24 | -0.06
NMW25 | -0.11
NMW26 | pending
NMW27 | pending
NMW30 | -0.15
NMW32 | -0.02
NMW33 | -0.08
NMW34 | pending
RHP01 | -0.04
RHP02 | -0.02
RHP03 | -0.02
RHP04A | -0.04
RHP04B | -0.06
RHP04C | -0.02
RHP05 | -0.15
RHP06 | -0.04
RHP07 | 0.00
RHP08 | -0.17
RHP08B | pending
RHP08C | pending
Not all wells currently have horizontal displacement correction factors. Horizontal displacement corrections will be updated once available.
Horizontal displacement cannot be calculated for RHMW01. RHMW01 is a 1-inch well, which is too narrow for the gyroscopic survey tool.